## CFM by Stack
Row Labels | Sum of Measured window closed, bath door closed, hall door closed (cfm)
26 | 193.9443
27 | 100.1088
28 | 170.7946
29 | 285.615
30 | 222.8371
31 | 240.1551
32 | 296.1736
33 | 237.5928
34 | 200.3943
37 | 221.5117
38 | 117.957
39 | 167.4371
40 | 205.6516
41 | 115.7039
42 | 251.6858
43 | 219.6121
44 | 257.2964
45 | 232.2913
46 | 297.9408
47 | 352.5456
49 | 67.0632
50 | 311.2386
Grand Total | 4765.5506

## Room Data
Floor N | Room NN | Room NNN | Rooftop Fan # | DWG CFM | DWG SP | DWG RPM | DWG HP | DWG (ILG) Model | DWG Source | DWG cfm/room | Wing | RM Area | RM Volume | Measured window closed, bath closed, hall closed (fpm) | Measured window open, bath open, hall closed (fpm) | Measured window closed, bath door closed, hall door closed (cfm) | Measured window open, bath door open, hall door closed (cfm) | Measured window closed, bath door closed, hall door closed (ACH) | Measured window open, bath door open, hall door closed (ACH) | Notes
1 | 1 | 101 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 422 | 3644.89 |  |  | 0 | 0 | 0 | 0 | Not collect from apartment
1 | 5 | 105 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 230 | 2050.8 | 455 | 530 | 20.1013 | 23.4147 | 0.5881 | 0.68504
1 | 6 | 106 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 222 | 2053.5 |  |  | 0 | 0 | 0 | 0 | Not collect from apartment
1 | 7 | 107 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 422 | 497 | 18.6434 | 21.9568 | 0.5818 | 0.6852
1 | 8 | 108 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 255 | 2358.75 |  |  | 0 | 0 | 0 | 0 | Not collect from apartment
1 | 9 | 109 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 466 | 506 | 20.5872 | 22.3544 | 0.64246 | 0.6976
1 | 10 | 110 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 402 | 448 | 17.7598 | 19.792 | 0.55422 | 0.61764
1 | 11 | 111 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 430 | 476 | 18.9968 | 21.029 | 0.59283 | 0.65624
1 | 12 | 112 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 425 | 484 | 18.7759 | 21.3825 | 0.58593 | 0.66727
1 | 13 | 113 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 430 | 510 | 18.9968 | 22.5311 | 0.59283 | 0.70312
1 | 14 | 114 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 380 | 404 | 16.7879 | 17.8482 | 0.52389 | 0.55698
1 | 15 | 115 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 408 | 430 | 18.0249 | 18.9968 | 0.5625 | 0.59283
1 | 16 | 116 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 369 | 437 | 16.3019 | 19.3061 | 0.42266 | 0.50055
1 | 17 | 117 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 133 | 208 | 5.8758 | 9.1892 | 0.18336 | 0.28676
1 | 19 | 119 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 352 | 412 | 15.5509 | 18.2016 | 0.48529 | 0.56801
2 | 2 | 202 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 192 | 265 | 8.4823 | 11.7073 | 0.37669 | 0.51991
2 | 4 | 204 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 294 | 335 | 12.9885 | 14.7998 | 0.58017 | 0.66108
2 | 5 | 205 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 210 | 204 | 9.2775 | 9.0124 | 0.28952 | 0.28125
2 | 6 | 206 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 206 | 266 | 9.1008 | 11.7515 | 0.28401 | 0.36673
2 | 7 | 207 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 223 | 221 | 9.8518 | 9.7635 | 0.30744 | 0.30469
2 | 8 | 208 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 244 | 378 | 10.7796 | 16.6995 | 0.33639 | 0.52114
2 | 9 | 209 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 236 | 286 | 10.4262 | 12.6351 | 0.32537 | 0.3943
2 | 10 | 210 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 208 | 306 | 9.1892 | 13.5187 | 0.28676 | 0.42187
2 | 11 | 211 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 282 | 261 | 12.4584 | 11.5306 | 0.38878 | 0.35983
2 | 12 | 212 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 284 | 486 | 12.5467 | 21.4708 | 0.39154 | 0.67003
2 | 13 | 213 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 389 | 459 | 17.1855 | 20.278 | 0.5363 | 0.63281
2 | 14 | 214 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 256 | 395 | 11.3097 | 17.4506 | 0.35294 | 0.54457
2 | 15 | 215 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 306 | 400 | 13.5187 | 17.6715 | 0.42187 | 0.55147
2 | 16 | 216 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 311 | 405 | 13.7396 | 17.8924 | 0.35623 | 0.4639
2 | 17 | 217 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 331 | 305 | 14.6231 | 13.4745 | 0.45634 | 0.42049 | original
2 | 17 | 217 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 261 | 274 | 11.5306 | 12.1049 | 0.35983 | 0.37775 | check
2 | 19 | 219 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 296 | 334 | 13.0769 | 14.7557 | 0.2922 | 0.32971
2 | 21 | 221 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 328 | 435 | 14.4906 | 19.2177 | 0.37318 | 0.49491
2 | 23 | 223 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 366 | 455 | 16.1694 | 20.1013 | 0.36598 | 0.45498
2 | 25 | 225 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 345 | 448 | 15.2416 | 19.792 | 0.7557 | 0.98131
2 | 27 | 227 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 203 | 243 | 8.9683 | 10.7354 | 0.1385 | 0.16579 | original
2 | 27 | 227 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 77 | 180 | 3.4018 | 7.9522 | 0.052534 | 0.12281 | check
2 | 29 | 229 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 214 | 279 | 9.4542 | 12.3258 | 0.24459 | 0.31889
2 | 30 | 230 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 | 197 | 256 | 8.7032 | 11.3097 | 0.38212 | 0.49656
2 | 31 | 231 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 310 | 523 | 13.6954 | 23.1054 | 0.42054 | 0.70948
2 | 32 | 232 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 345 | 544 | 15.2416 | 24.0332 | 0.47564 | 0.74999
2 | 33 | 233 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 537 | 13.6512 | 23.7239 | 0.42601 | 0.74034
2 | 34 | 234 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 383 | 562 | 16.9204 | 24.8284 | 0.52803 | 0.77481
2 | 35 | 235 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 324 | 546 | 14.3139 | 24.1215 | 0.44669 | 0.75275
2 | 36 | 236 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 329 | 613 | 14.5348 | 27.0815 | 0.45358 | 0.84512
2 | 37 | 237 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 541 | 13.6512 | 23.9006 | 0.42601 | 0.74586
2 | 38 | 238 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 561 | 13.6512 | 24.7842 | 0.42601 | 0.77343
2 | 39 | 239 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 363 | 605 | 16.0368 | 26.7281 | 0.50046 | 0.83409
2 | 40 | 240 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 240 | 494 | 10.6029 | 21.8243 | 0.33088 | 0.68106
2 | 41 | 241 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 392 | 622 | 17.318 | 27.4791 | 0.54044 | 0.85753
2 | 42 | 242 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 212 | 502 | 9.3659 | 22.1777 | 0.29228 | 0.69209
2 | 43 | 243 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 240 | 431 | 10.6029 | 19.041 | 0.48491 | 0.87082
2 | 44 | 244 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 233 | 460 | 10.2936 | 20.3222 | 0.25985 | 0.51301
2 | 45 | 245 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 242 | 439 | 10.6912 | 19.3944 | 0.49189 | 0.89231
2 | 46 | 246 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 155 | 326 | 6.8477 | 14.4022 | 0.16283 | 0.34247
2 | 47 | 247 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 263 | 414 | 11.619 | 18.29 | 0.53457 | 0.8415
3 | 2 | 302 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 275 | 442 | 12.1491 | 19.527 | 0.53953 | 0.86717
3 | 4 | 304 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 301 | 459 | 13.2978 | 20.278 | 0.59398 | 0.90577
3 | 5 | 305 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 246 | 407 | 10.8679 | 17.9807 | 0.33915 | 0.56112
3 | 6 | 306 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 356 | 466 | 15.7276 | 20.5872 | 0.4908 | 0.64246
3 | 7 | 307 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 298 | 466 | 13.1652 | 20.5872 | 0.41084 | 0.64246
3 | 8 | 308 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 339 | 507 | 14.9766 | 22.3986 | 0.46737 | 0.69898
3 | 9 | 309 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 355 | 479 | 15.6834 | 21.1616 | 0.48943 | 0.66038
3 | 10 | 310 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 334 | 485 | 14.7557 | 21.4266 | 0.46047 | 0.66865
3 | 11 | 311 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 379 | 539 | 16.7437 | 23.8123 | 0.52251 | 0.7431
3 | 12 | 312 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 279 | 567 | 12.3258 | 25.0493 | 0.38465 | 0.7817
3 | 13 | 313 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 296 | 418 | 13.0769 | 18.4667 | 0.40808 | 0.57628
3 | 14 | 314 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 224 | 398 | 9.896 | 17.5831 | 0.30882 | 0.54871
3 | 15 | 315 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 319 | 446 | 14.093 | 19.7037 | 0.43979 | 0.61488
3 | 16 | 316 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 257 | 440 | 11.3539 | 19.4386 | 0.29438 | 0.50399
3 | 17 | 317 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 337 | 431 | 14.8882 | 19.041 | 0.46461 | 0.5942
3 | 19 | 319 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 295 | 393 | 13.0327 | 17.3622 | 0.29121 | 0.38796
3 | 21 | 321 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 276 | 410 | 12.1933 | 18.1132 | 0.31401 | 0.46647
3 | 23 | 323 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 264 | 385 | 11.6632 | 17.0088 | 0.26399 | 0.38498
3 | 25 | 325 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 297 | 409 | 13.1211 | 18.0691 | 0.65056 | 0.89588
3 | 27 | 327 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 65 | 210 | 2.8716 | 9.2775 | 0.044347 | 0.14328 | orignial
3 | 27 | 327 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 190 | 203 | 8.3939 | 8.9683 | 0.12963 | 0.1385 | check
3 | 29 | 329 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 116 | 292 | 5.1247 | 12.9002 | 0.13258 | 0.33374 | original
3 | 29 | 329 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 202 | 209 | 8.9241 | 9.2333 | 0.23088 | 0.23888 | check
3 | 30 | 330 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 175 | 1335.25 | 256 | 314 | 11.3097 | 13.8721 | 0.50821 | 0.62335
3 | 31 | 331 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 308 | 450 | 13.607 | 19.8804 | 0.41782 | 0.61046
3 | 32 | 332 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 354 | 477 | 15.6392 | 21.0732 | 0.48805 | 0.65762
3 | 33 | 333 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 355 | 473 | 15.6834 | 20.8965 | 0.48943 | 0.65211
3 | 34 | 334 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 382 | 532 | 16.8762 | 23.503 | 0.52665 | 0.73345
3 | 35 | 335 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 367 | 456 | 16.2136 | 20.1455 | 0.50597 | 0.62867
3 | 36 | 336 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 305 | 445 | 13.4745 | 19.6595 | 0.42049 | 0.61351
3 | 37 | 337 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 382 | 521 | 16.8762 | 23.0171 | 0.52665 | 0.71828
3 | 38 | 338 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 297 | 459 | 13.1211 | 20.278 | 0.40946 | 0.63281
3 | 39 | 339 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 366 | 544 | 16.1694 | 24.0332 | 0.50459 | 0.74999
3 | 40 | 340 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 252 | 459 | 11.133 | 20.278 | 0.34742 | 0.63281
3 | 41 | 341 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 415 | 556 | 18.3341 | 24.5633 | 0.57215 | 0.76654 | original
3 | 41 | 341 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 379 | 397 | 16.7437 | 17.5389 | 0.52251 | 0.54733 | check
3 | 42 | 342 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 242 | 426 | 10.6912 | 18.8201 | 0.33364 | 0.58731
3 | 43 | 343 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 232 | 386 | 10.2494 | 17.053 | 0.46875 | 0.7799
3 | 44 | 344 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 234 | 416 | 10.3378 | 18.3783 | 0.26097 | 0.46394
3 | 45 | 345 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 226 | 447 | 9.9844 | 19.7479 | 0.45937 | 0.90857
3 | 46 | 346 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 260 | 426 | 11.4864 | 18.8201 | 0.27314 | 0.44752
3 | 47 | 347 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 273 | 457 | 12.0608 | 20.1896 | 0.5549 | 0.9289
4 | 2 | 402 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 364 | 444 | 16.081 | 19.6153 | 0.71414 | 0.8711
4 | 3 | 403 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 640 | 810 | 28.2743 | 35.7847 | 0.91034 | 1.1522
4 | 4 | 404 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 275 | 363 | 12.1491 | 16.0368 | 0.54267 | 0.71633
4 | 5 | 405 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 370 | 488 | 16.3461 | 21.5592 | 0.51011 | 0.67279
4 | 6 | 406 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 305 | 460 | 13.4745 | 20.3222 | 0.42049 | 0.63419
4 | 7 | 407 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 310 | 460 | 13.6954 | 20.3222 | 0.42739 | 0.63419
4 | 8 | 408 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 340 | 495 | 15.0207 | 21.8684 | 0.46875 | 0.68244
4 | 9 | 409 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 360 | 515 | 15.9043 | 22.752 | 0.49632 | 0.71001
4 | 10 | 410 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 240 | 449 | 10.6029 | 19.8362 | 0.33088 | 0.61902
4 | 11 | 411 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 453 | 570 | 20.0129 | 25.1818 | 0.62454 | 0.78584
4 | 12 | 412 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 220 | 456 | 9.7193 | 20.1455 | 0.30331 | 0.62867
4 | 13 | 413 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 205 | 385 | 9.0566 | 17.0088 | 0.28263 | 0.53079
4 | 14 | 414 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 140 | 450 | 6.185 | 19.8804 | 0.19301 | 0.6204
4 | 15 | 415 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 310 | 550 | 13.6954 | 24.2983 | 0.42739 | 0.75827
4 | 16 | 416 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 200 | 450 | 8.8357 | 19.8804 | 0.22909 | 0.51544
4 | 17 | 417 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 327 | 604 | 14.4464 | 26.6839 | 0.45082 | 0.83271
4 | 19 | 419 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 284 | 465 | 12.5467 | 20.5431 | 0.28036 | 0.45903
4 | 21 | 421 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 90 | 305 | 3.9761 | 13.4745 | 0.1024 | 0.34701
4 | 23 | 423 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 100 | 380 | 4.4179 | 16.7879 | 0.099995 | 0.37998
4 | 25 | 425 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 370 | 580 | 16.3461 | 25.6236 | 0.81046 | 1.2704
4 | 27 | 427 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 208 | 300 | 9.1892 | 13.2536 | 0.14191 | 0.20468
4 | 29 | 429 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 134 | 230 | 5.9199 | 10.1611 | 0.15316 | 0.26288
4 | 30 | 430 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 | 235 |  | 10.382 | 0 | 0.45583 | 0 | Couldn't reach window
4 | 31 | 431 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 270 | 390 | 11.9282 | 17.2297 | 0.36627 | 0.52906
4 | 32 | 432 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 350 | 530 | 15.4625 | 23.4147 | 0.48253 | 0.73069
4 | 33 | 433 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 378 | 520 | 16.6995 | 22.9729 | 0.52114 | 0.71691
4 | 34 | 434 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 390 | 480 | 17.2297 | 21.2058 | 0.53768 | 0.66176
4 | 35 | 435 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 405 | 545 | 17.8924 | 24.0774 | 0.55836 | 0.75137
4 | 36 | 436 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 343 | 535 | 15.1533 | 23.6356 | 0.47288 | 0.73759
4 | 37 | 437 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 440 | 580 | 19.4386 | 25.6236 | 0.60661 | 0.79963
4 | 38 | 438 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 270 | 400 | 11.9282 | 17.6715 | 0.37224 | 0.55147
4 | 39 | 439 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 362 | 527 | 15.9927 | 23.2821 | 0.49908 | 0.72656
4 | 40 | 440 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 300 | 476 | 13.2536 | 21.029 | 0.4136 | 0.65624
4 | 41 | 441 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 500 | 638 | 22.0893 | 28.186 | 0.68933 | 0.87959
4 | 42 | 442 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 96 | 350 | 4.2412 | 15.4625 | 0.13235 | 0.48253
4 | 43 | 443 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 157 | 397 | 6.936 | 17.5389 | 0.31721 | 0.80213
4 | 44 | 444 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 80 | 300 | 3.5343 | 13.2536 | 0.089219 | 0.33457
4 | 45 | 445 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 90 | 340 | 3.9761 | 15.0207 | 0.18293 | 0.69109
4 | 46 | 446 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 295 | 434 | 13.0327 | 19.1735 | 0.3099 | 0.45593
4 | 47 | 447 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 154 | 260 | 6.8035 | 11.4864 | 0.31302 | 0.52848
5 | 2 | 502 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 360 | 470 | 15.9043 | 20.764 | 0.70629 | 0.92211
5 | 3 | 503 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 880 | 1080 | 38.8772 | 47.7129 | 1.2517 | 1.5362 | original
5 | 3 | 503 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 881 | 802 | 38.9214 | 35.4313 | 1.2531 | 1.1408 | check
5 | 4 | 504 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 268 | 402 | 11.8399 | 17.7598 | 0.52886 | 0.79329
5 | 5 | 505 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 469 | 575 | 20.7198 | 25.4027 | 0.64659 | 0.79273
5 | 6 | 506 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 567 | 623 | 25.0493 | 27.5233 | 0.7817 | 0.85891
5 | 7 | 507 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 445 | 575 | 19.6595 | 25.4027 | 0.61351 | 0.79273
5 | 8 | 508 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 495 | 599 | 21.8684 | 26.463 | 0.68244 | 0.82582
5 | 9 | 509 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 500 | 663 | 22.0893 | 29.2904 | 0.68933 | 0.91406
5 | 10 | 510 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 391 | 455 | 17.2739 | 20.1013 | 0.53906 | 0.62729
5 | 11 | 511 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 543 | 670 | 23.989 | 29.5997 | 0.74862 | 0.92371
5 | 12 | 512 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 410 | 480 | 18.1132 | 21.2058 | 0.56525 | 0.66176
5 | 13 | 513 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 355 | 530 | 15.6834 | 23.4147 | 0.48943 | 0.73069
5 | 14 | 514 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 361 | 428 | 15.9485 | 18.9085 | 0.4977 | 0.59007
5 | 15 | 515 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 500 | 701 | 22.0893 | 30.9692 | 0.68933 | 0.96644
5 | 16 | 516 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 320 | 360 | 14.1372 | 15.9043 | 0.36654 | 0.41235
5 | 17 | 517 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 391 | 480 | 17.2739 | 21.2058 | 0.53906 | 0.66176
5 | 19 | 519 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 338 | 500 | 14.9324 | 22.0893 | 0.33366 | 0.49358
5 | 21 | 521 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 140 | 248 | 6.185 | 10.9563 | 0.15928 | 0.28216
5 | 23 | 523 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 134 | 328 | 5.9199 | 14.4906 | 0.13399 | 0.32798
5 | 25 | 525 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 432 | 695 | 19.0852 | 30.7042 | 0.94626 | 1.5223 | original
5 | 25 | 525 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 491 | 567 | 21.6917 | 25.0493 | 1.0755 | 1.242 | check
5 | 27 | 527 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 319 | 334 | 14.093 | 14.7557 | 0.21764 | 0.22788
5 | 29 | 529 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 300 | 370 | 13.2536 | 16.3461 | 0.34289 | 0.4229
5 | 30 | 530 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 |  |  | 0 | 0 | 0 | 0 | Not collected
5 | 31 | 531 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 432 | 555 | 19.0852 | 24.5191 | 0.58604 | 0.75289
5 | 32 | 532 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 567 | 760 | 25.0493 | 33.5758 | 0.7817 | 1.0478
5 | 33 | 533 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 280 | 354 | 12.37 | 15.6392 | 0.38603 | 0.48805
5 | 34 | 534 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 340 | 550 | 15.0207 | 24.2983 | 0.46875 | 0.75827
5 | 35 | 535 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 470 | 590 | 20.764 | 26.0654 | 0.64797 | 0.81341
5 | 36 | 536 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 400 | 410 | 17.6715 | 18.1132 | 0.55147 | 0.56525
5 | 37 | 537 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 580 | 640 | 25.6236 | 28.2743 | 0.79963 | 0.88235
5 | 38 | 538 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 380 | 660 | 16.7879 | 29.1579 | 0.52389 | 0.90992
5 | 39 | 539 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 555 | 570 | 24.5191 | 25.1818 | 0.76516 | 0.78584
5 | 40 | 540 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 582 | 532 | 25.712 | 23.503 | 0.80238 | 0.73345 | original
5 | 40 | 540 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 493 | 572 | 21.7801 | 25.2702 | 0.67968 | 0.7886 | check
5 | 41 | 541 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 467 | 650 | 20.6314 | 28.7161 | 0.64384 | 0.89613
5 | 42 | 542 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 200 | 355 | 8.8357 | 15.6834 | 0.27573 | 0.48943
5 | 43 | 543 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 128 | 300 | 5.6549 | 13.2536 | 0.25862 | 0.60614 | original
5 | 43 | 543 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 249 | 294 | 11.0005 | 12.9885 | 0.5031 | 0.59402 | check
5 | 44 | 544 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 270 | 500 | 11.9282 | 22.0893 | 0.30112 | 0.55762
5 | 45 | 545 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 105 | 380 | 4.6388 | 16.7879 | 0.21342 | 0.77239 | original
5 | 45 | 545 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 246 | 306 | 10.8679 | 13.5187 | 0.50002 | 0.62198 | check
5 | 46 | 546 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 435 | 586 | 19.2177 | 25.8887 | 0.45698 | 0.61561
5 | 47 | 547 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 182 | 300 | 8.0405 | 13.2536 | 0.36993 | 0.60978 | original
5 | 47 | 547 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 293 | 357 | 12.9443 | 15.7718 | 0.59555 | 0.72564 | check
6 | 2 | 602 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 677 | 773 | 29.9089 | 34.1501 | 1.3282 | 1.5166
6 | 3 | 603 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 830 | 944 | 36.6683 | 41.7046 | 1.1806 | 1.3428
6 | 4 | 604 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 525 | 570 | 23.1938 | 25.1818 | 1.036 | 1.1248
6 | 5 | 605 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 580 | 591 | 25.6236 | 26.1096 | 0.79963 | 0.81479
6 | 6 | 606 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 650 | 800 | 28.7161 | 35.3429 | 0.89613 | 1.1029
6 | 7 | 607 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 667 | 651 | 29.4672 | 28.7603 | 0.91957 | 0.89751 | original
6 | 7 | 607 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 464 | 642 | 20.4989 | 28.3627 | 0.6397 | 0.8851 | check
6 | 8 | 608 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 320 | 580 | 14.1372 | 25.6236 | 0.44117 | 0.79963
6 | 9 | 609 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 555 | 665 | 24.5191 | 29.3788 | 0.76516 | 0.91681
6 | 10 | 610 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 609 | 711 | 26.9048 | 31.411 | 0.83961 | 0.98023
6 | 11 | 611 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 560 | 571 | 24.74 | 25.226 | 0.77205 | 0.78722
6 | 12 | 612 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 422 | 444 | 18.6434 | 19.6153 | 0.5818 | 0.61213
6 | 13 | 613 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 365 | 383 | 16.1252 | 16.9204 | 0.50321 | 0.52803
6 | 14 | 614 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 545 | 660 | 24.0774 | 29.1579 | 0.75137 | 0.90992
6 | 15 | 615 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 504 | 520 | 22.266 | 22.9729 | 0.69485 | 0.71691
6 | 16 | 616 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 402 | 622 | 17.7598 | 27.4791 | 0.46046 | 0.71246
6 | 17 | 617 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 344 | 479 | 15.1975 | 21.1616 | 0.47426 | 0.66038
6 | 19 | 619 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 508 | 762 | 22.4428 | 33.6641 | 0.50148 | 0.75222
6 | 21 | 621 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 239 | 392 | 10.5587 | 17.318 | 0.27192 | 0.44599
6 | 23 | 623 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 369 | 468 | 16.3019 | 20.6756 | 0.36898 | 0.46798
6 | 25 | 625 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 685 | 677 | 30.2624 | 29.9089 | 1.5004 | 1.4829 | original
6 | 25 | 625 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 536 | 665 | 23.6798 | 29.3788 | 1.1741 | 1.4566 | check
6 | 27 | 627 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 708 | 744 | 31.2785 | 32.8689 | 0.48304 | 0.50761
6 | 29 | 629 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 562 | 627 | 24.8284 | 27.7 | 0.64234 | 0.71664
6 | 30 | 630 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 | 526 | 570 | 23.238 | 25.1818 | 1.0203 | 1.1056
6 | 31 | 631 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 386 | 501 | 17.053 | 22.1335 | 0.52363 | 0.67964
6 | 32 | 632 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 532 | 622 | 23.503 | 27.4791 | 0.73345 | 0.85753
6 | 33 | 633 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 538 | 613 | 23.7681 | 27.0815 | 0.74172 | 0.84512
6 | 34 | 634 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 570 | 855 | 25.1818 | 37.7727 | 0.78584 | 1.1788
6 | 35 | 635 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 510 | 573 | 22.5311 | 25.3144 | 0.70312 | 0.78998
6 | 36 | 636 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 560 | 645 | 24.74 | 28.4952 | 0.77205 | 0.88924
6 | 37 | 637 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 604 | 653 | 26.6839 | 28.8487 | 0.83271 | 0.90027
6 | 38 | 638 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 29 | 655 | 1.2812 | 28.937 | 0.039981 | 0.90303 | original
6 | 38 | 638 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 437 | 605 | 19.3061 | 26.7281 | 0.60248 | 0.83409 | check
6 | 39 | 639 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 485 | 404 | 21.4266 | 17.8482 | 0.66865 | 0.55698 | original
6 | 39 | 639 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 454 | 512 | 20.0571 | 22.6195 | 0.62591 | 0.70588 | check
6 | 40 | 640 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 1075 | 1111 | 47.492 | 49.0825 | 1.4821 | 1.5317
6 | 41 | 641 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 630 | 680 | 27.8325 | 30.0415 | 0.86856 | 0.93749
6 | 42 | 642 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 398 | 571 | 17.5831 | 25.226 | 0.54871 | 0.78722
6 | 43 | 643 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 79 | 254 | 3.4901 | 11.2214 | 0.15962 | 0.5132 | original
6 | 43 | 643 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 69 | 312 | 3.0483 | 13.7837 | 0.13941 | 0.63039 | check
6 | 44 | 644 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 317 | 522 | 14.0046 | 23.0613 | 0.35353 | 0.58216
6 | 45 | 645 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 191 | 394 | 8.4381 | 17.4064 | 0.38823 | 0.80085
6 | 46 | 646 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 730 | 859 | 32.2504 | 37.9495 | 0.76688 | 0.9024
6 | 47 | 647 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 306 | 474 | 13.5187 | 20.9407 | 0.62198 | 0.96345
7 | 2 | 702 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 1286 | 1649 | 56.8137 | 72.8506 | 2.523 | 3.2352 | original
7 | 2 | 702 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 1236 | 1294 | 54.6048 | 57.1672 | 2.4249 | 2.5387 | check
7 | 3 | 703 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 635 | 760 | 28.0534 | 33.5758 | 0.90323 | 1.081
7 | 4 | 704 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 603 | 727 | 26.6397 | 32.1179 | 1.1899 | 1.4346
7 | 5 | 705 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 620 | 788 | 27.3908 | 34.8128 | 0.85477 | 1.0864
7 | 6 | 706 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 657 | 758 | 29.0254 | 33.4874 | 0.90578 | 1.045
7 | 7 | 707 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 686 | 831 | 30.3066 | 36.7125 | 0.94576 | 1.1457
7 | 8 | 708 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 565 | 702 | 24.9609 | 31.0134 | 0.77895 | 0.96782
7 | 9 | 709 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 695 | 845 | 30.7042 | 37.331 | 0.95817 | 1.165
7 | 10 | 710 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 645 | 830 | 28.4952 | 36.6683 | 0.88924 | 1.1443
7 | 11 | 711 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 890 | 1052 | 39.319 | 46.4759 | 1.227 | 1.4504
7 | 12 | 712 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 567 | 768 | 25.0493 | 33.9292 | 0.7817 | 1.0588
7 | 13 | 713 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 559 | 679 | 24.6959 | 29.9973 | 0.77067 | 0.93611
7 | 14 | 714 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 338 | 475 | 14.9324 | 20.9849 | 0.46599 | 0.65487
7 | 15 | 715 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 432 | 539 | 19.0852 | 23.8123 | 0.59558 | 0.7431
7 | 16 | 716 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 433 | 651 | 19.1294 | 28.7603 | 0.49597 | 0.74567
7 | 17 | 717 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 344 | 415 | 15.1975 | 18.3341 | 0.47426 | 0.57215
7 | 19 | 719 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 473 | 564 | 20.8965 | 24.9168 | 0.46693 | 0.55676
7 | 21 | 721 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 75 | 275 | 3.3134 | 12.1491 | 0.08533 | 0.31288 | original
7 | 21 | 721 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 130 | 256 | 5.7432 | 11.3097 | 0.1479 | 0.29126 | check
7 | 23 | 723 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 16 | 320 | 0.70686 | 14.1372 | 0.015999 | 0.31998 | original
7 | 23 | 723 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 143 | 273 | 6.3175 | 12.0608 | 0.14299 | 0.27299 | check
7 | 25 | 725 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 634 | 699 | 28.0093 | 30.8809 | 1.3887 | 1.5311
7 | 27 | 727 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 750 | 924 | 33.134 | 40.8211 | 0.5117 | 0.63041
7 | 29 | 729 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 607 | 722 | 26.8164 | 31.897 | 0.69378 | 0.82522
7 | 30 | 730 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 | 1405 | 1435 | 62.071 | 63.3964 | 2.7253 | 2.7835
7 | 31 | 731 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 810 | 943 | 35.7847 | 41.6605 | 1.0988 | 1.2792
7 | 32 | 732 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 780 | 974 | 34.4593 | 43.03 | 1.0754 | 1.3428
7 | 33 | 733 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 595 | 680 | 26.2863 | 30.0415 | 0.82031 | 0.93749
7 | 34 | 734 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 704 | 721 | 31.1018 | 31.8528 | 0.97058 | 0.99402
7 | 35 | 735 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 664 | 789 | 29.3346 | 34.857 | 0.91543 | 1.0878
7 | 36 | 736 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 842 | 960 | 37.1984 | 42.4115 | 1.1608 | 1.3235
7 | 37 | 737 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 769 | 880 | 33.9734 | 38.8772 | 1.0602 | 1.2132
7 | 38 | 738 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 757 | 816 | 33.4432 | 36.0498 | 1.0436 | 1.125
7 | 39 | 739 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 637 | 838 | 28.1418 | 37.0217 | 0.87821 | 1.1553
7 | 40 | 740 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 828 | 872 | 36.5799 | 38.5238 | 1.1415 | 1.2022
7 | 41 | 741 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 739 | 836 | 32.648 | 36.9333 | 1.0188 | 1.1526
7 | 42 | 742 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 1671 | 1433 | 73.8225 | 63.308 | 2.3038 | 1.9756 | original
7 | 42 | 742 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 1391 | 1372 | 61.4525 | 60.6131 | 1.9177 | 1.8915 | check
7 | 43 | 743 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 187 | 290 | 8.2614 | 12.8118 | 0.37783 | 0.58594 | original
7 | 43 | 743 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 154 | 259 | 6.8035 | 11.4423 | 0.31115 | 0.5233 | check
7 | 44 | 744 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 384 | 566 | 16.9646 | 25.0051 | 0.42825 | 0.63123
7 | 45 | 745 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 239 | 430 | 10.5587 | 18.9968 | 0.48579 | 0.87402
7 | 46 | 746 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 472 | 524 | 20.8523 | 23.1496 | 0.49585 | 0.55047
7 | 47 | 747 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 393 | 551 | 17.3622 | 24.3424 | 0.79881 | 1.12
2 | 1 | 201
3 | 1 | 301
4 | 1 | 401
5 | 1 | 501
6 | 1 | 601
7 | 1 | 701
1 | 2 | 102
1 | 3 | 103
2 | 3 | 203
3 | 3 | 303
1 | 4 | 104
1 | 18 | 118
2 | 18 | 218
3 | 18 | 318
4 | 18 | 418
5 | 18 | 518
6 | 18 | 618
7 | 18 | 718
1 | 20 | 120
2 | 20 | 220
3 | 20 | 320
4 | 20 | 420
5 | 20 | 520
6 | 20 | 620
7 | 20 | 720
1 | 21 | 121
1 | 22 | 122
2 | 22 | 222
3 | 22 | 322
4 | 22 | 422
5 | 22 | 522
6 | 22 | 622
7 | 22 | 722
1 | 23 | 123
1 | 24 | 124
2 | 24 | 224
3 | 24 | 324
4 | 24 | 424
5 | 24 | 524
6 | 24 | 624
7 | 24 | 724
1 | 25 | 125
1 | 26 | 126
2 | 26 | 226
3 | 26 | 326
4 | 26 | 426
5 | 26 | 526
6 | 26 | 626
7 | 26 | 726
1 | 27 | 127
1 | 28 | 128
2 | 28 | 228
3 | 28 | 328
4 | 28 | 428
5 | 28 | 528
6 | 28 | 628
7 | 28 | 728
1 | 29 | 129
1 | 30 | 130
1 | 31 | 131
1 | 32 | 132
1 | 33 | 133
1 | 34 | 134
1 | 35 | 135
1 | 36 | 136
1 | 37 | 137
1 | 38 | 138
1 | 39 | 139
1 | 40 | 140
1 | 41 | 141
1 | 42 | 142
1 | 43 | 143
1 | 44 | 144
1 | 45 | 145
1 | 46 | 146
1 | 47 | 147

## Notes
Room dimensions from Barnhart_79.pdf and not physically checked.
Stack 50 need to confirm that all those rooms are on that stack.
Only missing 4 rooms that are attatched to stacks but were not sampled.
Rest Room air flow rates were measured by various people from to 3/26/21-7/9/21.
Dale spot checked and repeated some measurements to check, if the first one is close to the check then use it, if not use the checked values.
Measurements by TSI 9565p1623004 (last calibrated 8/2017) with probe 964p16180038 (last calibrated 4/2016) thus both are technically outside of calibration window.
When opening windows the air flow rate can go up or down depending on wind and stack effects.
Anecdotally facility people repaired items during the monitoring period. Specifics unknown.

## Sheet2
Floor N | Room NN | Room NNN | Rooftop Fan # | DWG CFM | DWG SP | DWG RPM | DWG HP | DWG (ILG) Model | DWG Source | DWG cfm/room | Wing | RM Area | RM Volume | Measured window closed, bath closed, hall closed (fpm) | Measured window open, bath open, hall closed (fpm) | Measured window closed, bath closed, hall closed (cfm) | Measured window open, bath open, hall closed (cfm) | Measured window closed, bath closed, hall closed (ACH) | Measured window open, bath open, hall closed (ACH) | Cleanup
1 | 1 | 101 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 422 | 3644.89 |  |  | 0 | 0 | 0 | 0 | cleanup
1 | 5 | 105 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 230 | 2050.8 | 455 | 530 | 20.1013 | 23.4147 | 0.5881 | 0.68504
1 | 6 | 106 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 222 | 2053.5 |  |  | 0 | 0 | 0 | 0 | cleanup
1 | 7 | 107 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 422 | 497 | 18.6434 | 21.9568 | 0.5818 | 0.6852
1 | 8 | 108 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 255 | 2358.75 |  |  | 0 | 0 | 0 | 0 | cleanup
1 | 9 | 109 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 466 | 506 | 20.5872 | 22.3544 | 0.64246 | 0.6976
1 | 10 | 110 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 402 | 448 | 17.7598 | 19.792 | 0.55422 | 0.61764
1 | 11 | 111 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 430 | 476 | 18.9968 | 21.029 | 0.59283 | 0.65624
1 | 12 | 112 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 425 | 484 | 18.7759 | 21.3825 | 0.58593 | 0.66727
1 | 13 | 113 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 430 | 510 | 18.9968 | 22.5311 | 0.59283 | 0.70312
1 | 14 | 114 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 380 | 404 | 16.7879 | 17.8482 | 0.52389 | 0.55698
1 | 15 | 115 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 408 | 430 | 18.0249 | 18.9968 | 0.5625 | 0.59283
1 | 16 | 116 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 369 | 437 | 16.3019 | 19.3061 | 0.42266 | 0.50055
1 | 17 | 117 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
1 | 19 | 119 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 352 | 412 | 15.5509 | 18.2016 | 0.48529 | 0.56801
2 | 2 | 202 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 4 | 204 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 5 | 205 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 6 | 206 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 7 | 207 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 8 | 208 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 9 | 209 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 10 | 210 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 11 | 211 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
2 | 12 | 212 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 284 | 486 | 12.5467 | 21.4708 | 0.39154 | 0.67003
2 | 13 | 213 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 389 | 459 | 17.1855 | 20.278 | 0.5363 | 0.63281
2 | 14 | 214 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 256 | 395 | 11.3097 | 17.4506 | 0.35294 | 0.54457
2 | 15 | 215 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 306 | 400 | 13.5187 | 17.6715 | 0.42187 | 0.55147
2 | 16 | 216 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 311 | 405 | 13.7396 | 17.8924 | 0.35623 | 0.4639
2 | 17 | 217 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 331 | 305 | 14.6231 | 13.4745 | 0.45634 | 0.42049 | check
2 | 19 | 219 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 296 | 334 | 13.0769 | 14.7557 | 0.2922 | 0.32971
2 | 21 | 221 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 328 | 435 | 14.4906 | 19.2177 | 0.37318 | 0.49491
2 | 23 | 223 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 366 | 455 | 16.1694 | 20.1013 | 0.36598 | 0.45498
2 | 25 | 225 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 345 | 448 | 15.2416 | 19.792 | 0.7557 | 0.98131
2 | 27 | 227 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 203 | 243 | 8.9683 | 10.7354 | 0.1385 | 0.16579 | check
2 | 29 | 229 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 214 | 279 | 9.4542 | 12.3258 | 0.24459 | 0.31889
2 | 30 | 230 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 | 257 |  | 11.3539 | 0 | 0.4985 | 0 | check
2 | 31 | 231 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 310 | 523 | 13.6954 | 23.1054 | 0.42054 | 0.70948
2 | 32 | 232 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 345 | 544 | 15.2416 | 24.0332 | 0.47564 | 0.74999
2 | 33 | 233 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 537 | 13.6512 | 23.7239 | 0.42601 | 0.74034
2 | 34 | 234 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 383 | 562 | 16.9204 | 24.8284 | 0.52803 | 0.77481
2 | 35 | 235 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 324 | 546 | 14.3139 | 24.1215 | 0.44669 | 0.75275
2 | 36 | 236 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 329 | 613 | 14.5348 | 27.0815 | 0.45358 | 0.84512
2 | 37 | 237 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 541 | 13.6512 | 23.9006 | 0.42601 | 0.74586
2 | 38 | 238 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 309 | 561 | 13.6512 | 24.7842 | 0.42601 | 0.77343
2 | 39 | 239 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 363 | 605 | 16.0368 | 26.7281 | 0.50046 | 0.83409
2 | 40 | 240 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 240 | 494 | 10.6029 | 21.8243 | 0.33088 | 0.68106
2 | 41 | 241 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 392 | 622 | 17.318 | 27.4791 | 0.54044 | 0.85753
2 | 42 | 242 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 212 | 502 | 9.3659 | 22.1777 | 0.29228 | 0.69209
2 | 43 | 243 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 240 | 431 | 10.6029 | 19.041 | 0.48491 | 0.87082
2 | 44 | 244 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 233 | 460 | 10.2936 | 20.3222 | 0.25985 | 0.51301
2 | 45 | 245 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 242 | 439 | 10.6912 | 19.3944 | 0.49189 | 0.89231
2 | 46 | 246 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 155 | 326 | 6.8477 | 14.4022 | 0.16283 | 0.34247 | check
2 | 47 | 247 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 263 | 414 | 11.619 | 18.29 | 0.53457 | 0.8415
3 | 2 | 302 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 275 | 442 | 12.1491 | 19.527 | 0.53953 | 0.86717
3 | 4 | 304 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 301 | 459 | 13.2978 | 20.278 | 0.59398 | 0.90577
3 | 5 | 305 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 246 | 407 | 10.8679 | 17.9807 | 0.33915 | 0.56112
3 | 6 | 306 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 356 | 466 | 15.7276 | 20.5872 | 0.4908 | 0.64246
3 | 7 | 307 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 298 | 466 | 13.1652 | 20.5872 | 0.41084 | 0.64246
3 | 8 | 308 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 339 | 507 | 14.9766 | 22.3986 | 0.46737 | 0.69898
3 | 9 | 309 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 355 | 479 | 15.6834 | 21.1616 | 0.48943 | 0.66038
3 | 10 | 310 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 334 | 485 | 14.7557 | 21.4266 | 0.46047 | 0.66865
3 | 11 | 311 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 379 | 539 | 16.7437 | 23.8123 | 0.52251 | 0.7431
3 | 12 | 312 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 279 | 567 | 12.3258 | 25.0493 | 0.38465 | 0.7817
3 | 13 | 313 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 296 | 418 | 13.0769 | 18.4667 | 0.40808 | 0.57628
3 | 14 | 314 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 224 | 398 | 9.896 | 17.5831 | 0.30882 | 0.54871
3 | 15 | 315 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 319 | 446 | 14.093 | 19.7037 | 0.43979 | 0.61488
3 | 16 | 316 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 257 | 440 | 11.3539 | 19.4386 | 0.29438 | 0.50399
3 | 17 | 317 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 337 | 431 | 14.8882 | 19.041 | 0.46461 | 0.5942
3 | 19 | 319 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 295 | 393 | 13.0327 | 17.3622 | 0.29121 | 0.38796
3 | 21 | 321 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 276 | 410 | 12.1933 | 18.1132 | 0.31401 | 0.46647
3 | 23 | 323 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 264 | 385 | 11.6632 | 17.0088 | 0.26399 | 0.38498
3 | 25 | 325 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 297 | 409 | 13.1211 | 18.0691 | 0.65056 | 0.89588
3 | 27 | 327 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 65 | 210 | 2.8716 | 9.2775 | 0.044347 | 0.14328 | check
3 | 29 | 329 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 116 | 292 | 5.1247 | 12.9002 | 0.13258 | 0.33374 | check
3 | 30 | 330 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 175 | 1335.25 |  |  | 0 | 0 | 0 | 0 | cleanup
3 | 31 | 331 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 308 | 450 | 13.607 | 19.8804 | 0.41782 | 0.61046
3 | 32 | 332 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 354 | 477 | 15.6392 | 21.0732 | 0.48805 | 0.65762
3 | 33 | 333 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 355 | 473 | 15.6834 | 20.8965 | 0.48943 | 0.65211
3 | 34 | 334 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 382 | 532 | 16.8762 | 23.503 | 0.52665 | 0.73345
3 | 35 | 335 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 367 | 456 | 16.2136 | 20.1455 | 0.50597 | 0.62867
3 | 36 | 336 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 305 | 445 | 13.4745 | 19.6595 | 0.42049 | 0.61351
3 | 37 | 337 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 382 | 521 | 16.8762 | 23.0171 | 0.52665 | 0.71828
3 | 38 | 338 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 297 | 459 | 13.1211 | 20.278 | 0.40946 | 0.63281
3 | 39 | 339 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 366 | 544 | 16.1694 | 24.0332 | 0.50459 | 0.74999
3 | 40 | 340 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 252 | 459 | 11.133 | 20.278 | 0.34742 | 0.63281
3 | 41 | 341 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 415 | 556 | 18.3341 | 24.5633 | 0.57215 | 0.76654 | check
3 | 42 | 342 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 242 | 426 | 10.6912 | 18.8201 | 0.33364 | 0.58731
3 | 43 | 343 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 232 | 386 | 10.2494 | 17.053 | 0.46875 | 0.7799
3 | 44 | 344 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 234 | 416 | 10.3378 | 18.3783 | 0.26097 | 0.46394
3 | 45 | 345 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 226 | 447 | 9.9844 | 19.7479 | 0.45937 | 0.90857
3 | 46 | 346 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 260 | 426 | 11.4864 | 18.8201 | 0.27314 | 0.44752
3 | 47 | 347 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 273 | 457 | 12.0608 | 20.1896 | 0.5549 | 0.9289
4 | 2 | 402 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 |  |  | 0 | 0 | 0 | 0 | cleanup
4 | 3 | 403 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 |  |  | 0 | 0 | 0 | 0 | cleanup
4 | 4 | 404 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 |  |  | 0 | 0 | 0 | 0 | cleanup
4 | 5 | 405 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 370 | 488 | 16.3461 | 21.5592 | 0.51011 | 0.67279
4 | 6 | 406 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 305 | 460 | 13.4745 | 20.3222 | 0.42049 | 0.63419
4 | 7 | 407 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 310 | 460 | 13.6954 | 20.3222 | 0.42739 | 0.63419
4 | 8 | 408 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 340 | 495 | 15.0207 | 21.8684 | 0.46875 | 0.68244
4 | 9 | 409 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 360 | 515 | 15.9043 | 22.752 | 0.49632 | 0.71001
4 | 10 | 410 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 240 | 449 | 10.6029 | 19.8362 | 0.33088 | 0.61902
4 | 11 | 411 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 453 | 570 | 20.0129 | 25.1818 | 0.62454 | 0.78584
4 | 12 | 412 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 220 | 456 | 9.7193 | 20.1455 | 0.30331 | 0.62867
4 | 13 | 413 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 205 | 385 | 9.0566 | 17.0088 | 0.28263 | 0.53079
4 | 14 | 414 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 140 | 450 | 6.185 | 19.8804 | 0.19301 | 0.6204
4 | 15 | 415 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 310 | 550 | 13.6954 | 24.2983 | 0.42739 | 0.75827
4 | 16 | 416 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 200 | 450 | 8.8357 | 19.8804 | 0.22909 | 0.51544
4 | 17 | 417 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 327 | 604 | 14.4464 | 26.6839 | 0.45082 | 0.83271
4 | 19 | 419 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 284 | 465 | 12.5467 | 20.5431 | 0.28036 | 0.45903
4 | 21 | 421 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 90 | 305 | 3.9761 | 13.4745 | 0.1024 | 0.34701
4 | 23 | 423 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 100 | 380 | 4.4179 | 16.7879 | 0.099995 | 0.37998
4 | 25 | 425 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 370 | 580 | 16.3461 | 25.6236 | 0.81046 | 1.2704
4 | 27 | 427 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 208 | 300 | 9.1892 | 13.2536 | 0.14191 | 0.20468
4 | 29 | 429 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 134 | 230 | 5.9199 | 10.1611 | 0.15316 | 0.26288
4 | 30 | 430 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 |  |  | 0 | 0 | 0 | 0 | cleanup
4 | 31 | 431 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 270 | 390 | 11.9282 | 17.2297 | 0.36627 | 0.52906
4 | 32 | 432 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 350 | 530 | 15.4625 | 23.4147 | 0.48253 | 0.73069
4 | 33 | 433 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 378 | 520 | 16.6995 | 22.9729 | 0.52114 | 0.71691
4 | 34 | 434 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 390 | 480 | 17.2297 | 21.2058 | 0.53768 | 0.66176
4 | 35 | 435 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 405 | 545 | 17.8924 | 24.0774 | 0.55836 | 0.75137
4 | 36 | 436 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 343 | 535 | 15.1533 | 23.6356 | 0.47288 | 0.73759
4 | 37 | 437 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 440 | 580 | 19.4386 | 25.6236 | 0.60661 | 0.79963
4 | 38 | 438 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 270 | 400 | 11.9282 | 17.6715 | 0.37224 | 0.55147
4 | 39 | 439 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 362 | 527 | 15.9927 | 23.2821 | 0.49908 | 0.72656
4 | 40 | 440 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 300 | 476 | 13.2536 | 21.029 | 0.4136 | 0.65624
4 | 41 | 441 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 500 | 638 | 22.0893 | 28.186 | 0.68933 | 0.87959
4 | 42 | 442 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 96 | 350 | 4.2412 | 15.4625 | 0.13235 | 0.48253
4 | 43 | 443 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 157 | 397 | 6.936 | 17.5389 | 0.31721 | 0.80213
4 | 44 | 444 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 80 | 300 | 3.5343 | 13.2536 | 0.089219 | 0.33457
4 | 45 | 445 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 90 | 340 | 3.9761 | 15.0207 | 0.18293 | 0.69109
4 | 46 | 446 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 295 | 434 | 13.0327 | 19.1735 | 0.3099 | 0.45593
4 | 47 | 447 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 154 | 260 | 6.8035 | 11.4864 | 0.31302 | 0.52848
5 | 2 | 502 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 360 | 470 | 15.9043 | 20.764 | 0.70629 | 0.92211
5 | 3 | 503 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 880 | 1080 | 38.8772 | 47.7129 | 1.2517 | 1.5362 | check
5 | 4 | 504 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 268 | 402 | 11.8399 | 17.7598 | 0.52886 | 0.79329
5 | 5 | 505 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 469 | 575 | 20.7198 | 25.4027 | 0.64659 | 0.79273
5 | 6 | 506 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 567 | 623 | 25.0493 | 27.5233 | 0.7817 | 0.85891
5 | 7 | 507 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 445 | 575 | 19.6595 | 25.4027 | 0.61351 | 0.79273
5 | 8 | 508 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 495 | 599 | 21.8684 | 26.463 | 0.68244 | 0.82582
5 | 9 | 509 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 500 | 663 | 22.0893 | 29.2904 | 0.68933 | 0.91406
5 | 10 | 510 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 391 | 455 | 17.2739 | 20.1013 | 0.53906 | 0.62729
5 | 11 | 511 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 543 | 670 | 23.989 | 29.5997 | 0.74862 | 0.92371
5 | 12 | 512 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 410 | 480 | 18.1132 | 21.2058 | 0.56525 | 0.66176
5 | 13 | 513 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 355 | 530 | 15.6834 | 23.4147 | 0.48943 | 0.73069
5 | 14 | 514 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 361 | 428 | 15.9485 | 18.9085 | 0.4977 | 0.59007
5 | 15 | 515 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 500 | 701 | 22.0893 | 30.9692 | 0.68933 | 0.96644
5 | 16 | 516 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 320 | 360 | 14.1372 | 15.9043 | 0.36654 | 0.41235
5 | 17 | 517 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 391 | 480 | 17.2739 | 21.2058 | 0.53906 | 0.66176
5 | 19 | 519 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 338 | 500 | 14.9324 | 22.0893 | 0.33366 | 0.49358
5 | 21 | 521 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 140 | 248 | 6.185 | 10.9563 | 0.15928 | 0.28216
5 | 23 | 523 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 134 | 328 | 5.9199 | 14.4906 | 0.13399 | 0.32798
5 | 25 | 525 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 432 | 695 | 19.0852 | 30.7042 | 0.94626 | 1.5223 | check
5 | 27 | 527 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 247 |  | 10.9121 | 0 | 0.16852 | 0 | check
5 | 29 | 529 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 300 | 370 | 13.2536 | 16.3461 | 0.34289 | 0.4229
5 | 30 | 530 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 31 | 531 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 432 | 555 | 19.0852 | 24.5191 | 0.58604 | 0.75289
5 | 32 | 532 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 33 | 533 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 280 | 354 | 12.37 | 15.6392 | 0.38603 | 0.48805
5 | 34 | 534 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 340 | 550 | 15.0207 | 24.2983 | 0.46875 | 0.75827
5 | 35 | 535 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 470 | 590 | 20.764 | 26.0654 | 0.64797 | 0.81341
5 | 36 | 536 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 400 | 410 | 17.6715 | 18.1132 | 0.55147 | 0.56525
5 | 37 | 537 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 580 | 640 | 25.6236 | 28.2743 | 0.79963 | 0.88235
5 | 38 | 538 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 39 | 539 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 40 | 540 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 41 | 541 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 42 | 542 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 43 | 543 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 44 | 544 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 45 | 545 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 46 | 546 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 |  |  | 0 | 0 | 0 | 0 | cleanup
5 | 47 | 547 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 |  |  | 0 | 0 | 0 | 0 | cleanup
6 | 2 | 602 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 677 | 773 | 29.9089 | 34.1501 | 1.3282 | 1.5166
6 | 3 | 603 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 830 | 944 | 36.6683 | 41.7046 | 1.1806 | 1.3428
6 | 4 | 604 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 525 | 570 | 23.1938 | 25.1818 | 1.036 | 1.1248
6 | 5 | 605 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 580 | 591 | 25.6236 | 26.1096 | 0.79963 | 0.81479
6 | 6 | 606 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 650 | 800 | 28.7161 | 35.3429 | 0.89613 | 1.1029
6 | 7 | 607 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 667 | 651 | 29.4672 | 28.7603 | 0.91957 | 0.89751 | check
6 | 8 | 608 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 320 | 580 | 14.1372 | 25.6236 | 0.44117 | 0.79963
6 | 9 | 609 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 555 | 665 | 24.5191 | 29.3788 | 0.76516 | 0.91681
6 | 10 | 610 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 609 | 711 | 26.9048 | 31.411 | 0.83961 | 0.98023
6 | 11 | 611 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 560 | 571 | 24.74 | 25.226 | 0.77205 | 0.78722
6 | 12 | 612 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 422 | 444 | 18.6434 | 19.6153 | 0.5818 | 0.61213
6 | 13 | 613 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 365 | 383 | 16.1252 | 16.9204 | 0.50321 | 0.52803
6 | 14 | 614 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 545 | 660 | 24.0774 | 29.1579 | 0.75137 | 0.90992
6 | 15 | 615 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 504 | 520 | 22.266 | 22.9729 | 0.69485 | 0.71691
6 | 16 | 616 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 402 | 622 | 17.7598 | 27.4791 | 0.46046 | 0.71246
6 | 17 | 617 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 344 | 479 | 15.1975 | 21.1616 | 0.47426 | 0.66038
6 | 19 | 619 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 508 | 762 | 22.4428 | 33.6641 | 0.50148 | 0.75222
6 | 21 | 621 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 239 | 392 | 10.5587 | 17.318 | 0.27192 | 0.44599
6 | 23 | 623 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 369 | 468 | 16.3019 | 20.6756 | 0.36898 | 0.46798
6 | 25 | 625 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 685 | 677 | 30.2624 | 29.9089 | 1.5004 | 1.4829 | check
6 | 27 | 627 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 708 | 744 | 31.2785 | 32.8689 | 0.48304 | 0.50761
6 | 29 | 629 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 562 | 627 | 24.8284 | 27.7 | 0.64234 | 0.71664
6 | 30 | 630 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 |  |  | 0 | 0 | 0 | 0 | cleanup
6 | 31 | 631 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 386 | 501 | 17.053 | 22.1335 | 0.52363 | 0.67964
6 | 32 | 632 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 532 | 622 | 23.503 | 27.4791 | 0.73345 | 0.85753
6 | 33 | 633 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 538 | 613 | 23.7681 | 27.0815 | 0.74172 | 0.84512
6 | 34 | 634 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 570 | 855 | 25.1818 | 37.7727 | 0.78584 | 1.1788
6 | 35 | 635 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 510 | 573 | 22.5311 | 25.3144 | 0.70312 | 0.78998
6 | 36 | 636 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 560 | 645 | 24.74 | 28.4952 | 0.77205 | 0.88924
6 | 37 | 637 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 604 | 653 | 26.6839 | 28.8487 | 0.83271 | 0.90027
6 | 38 | 638 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 29 | 655 | 1.2812 | 28.937 | 0.039981 | 0.90303 | check
6 | 39 | 639 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 485 | 404 | 21.4266 | 17.8482 | 0.66865 | 0.55698 | check
6 | 40 | 640 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 1075 | 1111 | 47.492 | 49.0825 | 1.4821 | 1.5317
6 | 41 | 641 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 630 | 680 | 27.8325 | 30.0415 | 0.86856 | 0.93749
6 | 42 | 642 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 398 | 571 | 17.5831 | 25.226 | 0.54871 | 0.78722
6 | 43 | 643 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 79 | 254 | 3.4901 | 11.2214 | 0.15962 | 0.5132 | check
6 | 44 | 644 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 317 | 522 | 14.0046 | 23.0613 | 0.35353 | 0.58216
6 | 45 | 645 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 191 | 394 | 8.4381 | 17.4064 | 0.38823 | 0.80085
6 | 46 | 646 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 730 | 859 | 32.2504 | 37.9495 | 0.76688 | 0.9024
6 | 47 | 647 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 306 | 474 | 13.5187 | 20.9407 | 0.62198 | 0.96345
7 | 2 | 702 | 26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 176 | 1351.08 | 1286 | 1649 | 56.8137 | 72.8506 | 2.523 | 3.2352 | check
7 | 3 | 703 | 28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 | 1966 Mechanical Details M5 | 37.5 | North | 238 | 1863.54 | 635 | 760 | 28.0534 | 33.5758 | 0.90323 | 1.081
7 | 4 | 704 | 27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 30 | North | 175 | 1343.25 | 603 | 727 | 26.6397 | 32.1179 | 1.1899 | 1.4346
7 | 5 | 705 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 620 | 788 | 27.3908 | 34.8128 | 0.85477 | 1.0864
7 | 6 | 706 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 657 | 758 | 29.0254 | 33.4874 | 0.90578 | 1.045
7 | 7 | 707 | 29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 686 | 831 | 30.3066 | 36.7125 | 0.94576 | 1.1457
7 | 8 | 708 | 30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 36.9231 | North | 249 | 1922.67 | 565 | 702 | 24.9609 | 31.0134 | 0.77895 | 0.96782
7 | 9 | 709 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 695 | 845 | 30.7042 | 37.331 | 0.95817 | 1.165
7 | 10 | 710 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 645 | 830 | 28.4952 | 36.6683 | 0.88924 | 1.1443
7 | 11 | 711 | 32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 890 | 1052 | 39.319 | 46.4759 | 1.227 | 1.4504
7 | 12 | 712 | 31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 567 | 768 | 25.0493 | 33.9292 | 0.7817 | 1.0588
7 | 13 | 713 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 559 | 679 | 24.6959 | 29.9973 | 0.77067 | 0.93611
7 | 14 | 714 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 338 | 475 | 14.9324 | 20.9849 | 0.46599 | 0.65487
7 | 15 | 715 | 33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 432 | 539 | 19.0852 | 23.8123 | 0.59558 | 0.7431
7 | 16 | 716 | 34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2314.17 | 433 | 651 | 19.1294 | 28.7603 | 0.49597 | 0.74567
7 | 17 | 717 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 249 | 1922.67 | 344 | 415 | 15.1975 | 18.3341 | 0.47426 | 0.57215
7 | 19 | 719 | 37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 346 | 2685.18 | 473 | 564 | 20.8965 | 24.9168 | 0.46693 | 0.55676
7 | 21 | 721 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 301 | 2329.83 | 75 | 275 | 3.3134 | 12.1491 | 0.08533 | 0.31288 | check
7 | 23 | 723 | 38 | 240 | 0.5 | 1000 | - | csp-a410 | 2010 M2.3 | 20 | North | 342 | 2650.86 | 16 | 320 | 0.70686 | 14.1372 | 0.015999 | 0.31998 | cleanup
7 | 25 | 725 | 39 | 480 | 0.5 | 1080 | - | csp-a710 | 2010 M2.3 | 80 | North | 158 | 1210.14 | 634 | 699 | 28.0093 | 30.8809 | 1.3887 | 1.5311
7 | 27 | 727 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 499 | 3885.17 | 750 | 924 | 33.134 | 40.8211 | 0.5117 | 0.63041
7 | 29 | 729 | 40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | North | 299 | 2319.17 | 607 | 722 | 26.8164 | 31.897 | 0.69378 | 0.82522
7 | 30 | 730 | 41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 179 | 1366.57 |  |  | 0 | 0 | 0 | 0 | cleanup
7 | 31 | 731 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 253 | 1953.99 | 810 | 943 | 35.7847 | 41.6605 | 1.0988 | 1.2792
7 | 32 | 732 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 780 | 974 | 34.4593 | 43.03 | 1.0754 | 1.3428
7 | 33 | 733 | 43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 595 | 680 | 26.2863 | 30.0415 | 0.82031 | 0.93749
7 | 34 | 734 | 42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 704 | 721 | 31.1018 | 31.8528 | 0.97058 | 0.99402
7 | 35 | 735 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 664 | 789 | 29.3346 | 34.857 | 0.91543 | 1.0878
7 | 36 | 736 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 842 | 960 | 37.1984 | 42.4115 | 1.1608 | 1.3235
7 | 37 | 737 | 44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 769 | 880 | 33.9734 | 38.8772 | 1.0602 | 1.2132
7 | 38 | 738 | 45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 757 | 816 | 33.4432 | 36.0498 | 1.0436 | 1.125
7 | 39 | 739 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 637 | 838 | 28.1418 | 37.0217 | 0.87821 | 1.1553
7 | 40 | 740 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 828 | 872 | 36.5799 | 38.5238 | 1.1415 | 1.2022
7 | 41 | 741 | 46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 739 | 836 | 32.648 | 36.9333 | 1.0188 | 1.1526
7 | 42 | 742 | 47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 | 1966 Mechanical Details M5 | 40 | South | 249 | 1922.67 | 1671 | 1433 | 73.8225 | 63.308 | 2.3038 | 1.9756 | check
7 | 43 | 743 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 171 | 1311.93 | 187 | 290 | 8.2614 | 12.8118 | 0.37783 | 0.58594 | check
7 | 44 | 744 | 49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 160 | South | 307 | 2376.81 | 384 | 566 | 16.9646 | 25.0051 | 0.42825 | 0.63123
7 | 45 | 745 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 239 | 430 | 10.5587 | 18.9968 | 0.48579 | 0.87402
7 | 46 | 746 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 328 | 2523.24 | 472 | 524 | 20.8523 | 23.1496 | 0.49585 | 0.55047
7 | 47 | 747 | 50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | 1966 Mechanical Details M5 | 10 | South | 170 | 1304.1 | 393 | 551 | 17.3622 | 24.3424 | 0.79881 | 1.12

## Dwg data
Rooftop Fan # | CFM | SP | RPM | HP | (ILG) Model | Note | Source | Wing | Number of rooms | dwg cfm/room | Rooms
26 | 240 | 0.25 | 975 | 0.033333 | crf-a100 |  | 1966 Mechanical Details M5 | North | 6 | 40 | 202, 302, 402, 502, 602, 702
27 | 240 | 0.25 | 975 | 0.033333 | crf-a100 |  | 1966 Mechanical Details M5 | North | 8 | 30 | 101, 106, 204, 304, 404, 504, 604, 704
28 | 150 | 0.25 | 1550 | 0.014286 | crf-a67 |  | 1966 Mechanical Details M5 | North | 4 | 37.5 | 403, 503, 603, 703
29 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 105, 107, 205, 207, 305, 307, 405, 407, 505, 507, 605, 607, 705, 707
30 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 13 | 36.9231 | 108, 206, 208, 306, 308, 406, 408, 506, 508, 606, 608, 706, 708
31 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 110, 112, 210, 212, 310, 312, 410, 412, 510, 512, 610, 612,710, 712
32 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 109, 111, 209, 211, 309, 311, 409, 411, 509, 511, 609, 611, 709, 711
33 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 113, 115, 213, 215, 313, 315, 413, 415, 513, 515, 613, 615, 713, 715
34 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 114, 116, 214, 216, 314, 316, 414, 416, 514, 516, 614, 616, 714, 716
35 | [7 empty] | North |  | #DIV/0! | Not toilet room exhaust
36 | [7 empty] | North |  | #DIV/0! | Not toilet room exhaust
37 | 560 | 0.25 | 1475 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 14 | 40 | 117, 119, 217, 219, 317, 319, 417, 419, 517, 519, 617, 619, 717, 719
38 | 240 | 0.5 | 1000 | - | csp-a410 | There are two exhaust vents on the roof of the mechanical penthouse that will need to be identified and mapped to a stack of rooms. These two will also have to be sampled slightly differently, as sampling won’t occur at the fan shroud like the others. | 2010 M2.3 | North | 12 | 20 | 221, 223, 321, 323, 421, 423, 521, 523, 621, 623, 721, 723
39 | 480 | 0.5 | 1080 | - | csp-a710 | There are two exhaust vents on the roof of the mechanical penthouse that will need to be identified and mapped to a stack of rooms. These two will also have to be sampled slightly differently, as sampling won’t occur at the fan shroud like the others. | 2010 M2.3 | North | 6 | 80 | 225, 325, 425, 525, 625, 725
40 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | North | 12 | 40 | 227, 229, 327, 329, 427, 429, 527, 529, 627, 629, 727,729
41 | 240 | 0.25 | 975 | 0.033333 | crf-a100 |  | 1966 Mechanical Details M5 | South | 6 | 40 | 230, 330, 430, 530, 630, 730
42 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 232, 234, 332, 334, 432, 434, 532, 534, 632, 634, 732, 734
43 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 231, 233, 331, 333, 431, 433, 531, 533, 631, 633, 731, 733
44 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 235, 237, 335, 337, 435, 437, 535, 537, 635, 637, 735, 737
45 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 236, 238, 336, 338, 436, 438, 536, 538, 636, 638, 736, 738
46 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 239, 241, 339, 341, 439, 441, 539, 541, 639, 641, 739, 741
47 | 480 | 0.25 | 1300 | 0.1 | crf-a100 |  | 1966 Mechanical Details M5 | South | 12 | 40 | 240, 242, 340, 342, 440, 442, 540, 542, 640, 642, 740, 742
48 | 300 | 0.25 | 1550 | 0.04 | crf-a82 |  | 1966 Mechanical Details M5 | South |  | #DIV/0! | Not toilet room exhaust
49 | 960 | 0.5 | 1100 | 0.16667 | bca-1225 |  | 1966 Mechanical Details M5 | South | 6 | 160 | 244, 344, 444, 544, 644, 744
50 | 240 | 0.25 | 600 | 0.16667 | bca-1225 | Facilities best assumption/recollection is that EF-50 serves a lot of rooms. The most of any exhaust fan in fact. Since I know that particular fan is where you started exhaust sampling, it would be good to confirm all those rooms are really on a single stack. This can be confirmed by switching #50 in the 728 electrical room, provided you have an empty room in the 43, 45, 47 stack. | 1966 Mechanical Details M5 | South | 24 | 10 | 243, 245, 246, 247, 343, 345, 346, 347, 443, 445, 446, 447, 543, 545, 546, 547, 643, 645, 646, 647, 743, 745, 746, 747
We know window and door operation have a big impact. Since we are not logging coincident to sampling, capturing air speed at the room exhaust for each condition will be the best we can do. At the moment, it’s a fair assumption that all fans are trying to pull the same, but you can see some serve 4 rooms and some potentially 24 rooms. That probably results in pretty significant variation in air exchange rate between rooms, and it would be good to document that.

## Sheet1
Row Labels | Count of Mod room | Sum of SQ.FT. | Sum of Volume
1 | 2 | 131 | 1310
3 | 2 | 131 | 1310
10 | 2 | 630 | 6507.9
20 | 1 | 722 | 12996
21 | 2 | 916 | 16488
22 | 3 | 908 | 7584.05
23 | 1 | 35 | 274.05
24 | 1 | 42 | 433.86
25 | 2 | 184 | 1472
26 | 1 | 295 | 2336.4
28 | 1 | 171 | 1368
29 | 2 | 80 | 640
30 | 1 | 315 | 2781.45
32 | 1 | 574 | 5068.42
40 | 1 | 893 | 9224.69
41 | 4 | 591 | 4722.6
42 | 1 | 78 | 688.74
43 | 1 | 266 | 2128
44 | 1 | 103 | 909.49
45 | 6 | 469 | 3752
46 | 3 | 1541 | 29266
47 | 1 | 140 | 2800
51 | 1 | 115 | 1150
53 | 1 | 115 | 1150
101 | 5 | 422 | 3644.89
102 | 1 | 264 | 2442
103 | 1 | 129 | 1032
105 | 4 | 230 | 2050.8
106 | 3 | 222 | 2053.5
107 | 3 | 249 | 1922.67
108 | 3 | 255 | 2358.75
109 | 3 | 249 | 1922.67
110 | 3 | 249 | 1922.67
111 | 3 | 249 | 1922.67
112 | 3 | 249 | 1922.67
113 | 3 | 249 | 1922.67
114 | 3 | 249 | 1922.67
115 | 3 | 249 | 1922.67
116 | 3 | 299 | 2314.17
117 | 3 | 249 | 1922.67
118 | 1 | 44 | 352
119 | 3 | 249 | 1922.67
120 | 1 | 62 | 573.5
121 | 1 | 57 | 527.25
122 | 5 | 1511 | 13559.69
123 | 1 | 35 | 274.05
128 | 2 | 137 | 1085.04
129 | 1 | 9 | 70.47
130 | 1 | 35 | 274.05
131 | 1 | 105 | 822.15
132 | 1 | 15 | 117.45
133 | 2 | 82 | 642.06
134 | 1 | 49 | 383.67
135 | 1 | 100 | 783
136 | 2 | 1600 | 12528
146 | 1 | 83 | 830
151 | 1 | 131 | 1048
153 | 1 | 131 | 1048
201 | 2 | 142 | 1133.79
202 | 3 | 176 | 1351.08
203 | 3 | 206 | 1635.08
204 | 3 | 175 | 1343.25
205 | 3 | 249 | 1922.67
206 | 3 | 249 | 1922.67
207 | 3 | 249 | 1922.67
208 | 3 | 249 | 1922.67
209 | 3 | 249 | 1922.67
210 | 3 | 249 | 1922.67
211 | 3 | 249 | 1922.67
212 | 3 | 249 | 1922.67
213 | 3 | 249 | 1922.67
214 | 3 | 249 | 1922.67
215 | 3 | 249 | 1922.67
216 | 3 | 299 | 2314.17
217 | 3 | 249 | 1922.67
218 | 1 | 44 | 352
219 | 3 | 346 | 2685.18
220 | 1 | 95 | 760
221 | 3 | 301 | 2329.83
222 | 7 | 1331 | 11770.51
223 | 4 | 342 | 2650.86
225 | 3 | 158 | 1210.14
227 | 4 | 499 | 3885.17
228 | 3 | 209 | 1648.8
229 | 3 | 299 | 2319.17
230 | 3 | 179 | 1366.57
231 | 3 | 253 | 1953.99
232 | 3 | 249 | 1922.67
233 | 3 | 249 | 1922.67
234 | 3 | 249 | 1922.67
235 | 3 | 249 | 1922.67
236 | 3 | 249 | 1922.67
237 | 3 | 249 | 1922.67
238 | 3 | 249 | 1922.67
239 | 3 | 249 | 1922.67
240 | 3 | 249 | 1922.67
241 | 3 | 249 | 1922.67
242 | 3 | 249 | 1922.67
243 | 3 | 171 | 1311.93
244 | 3 | 307 | 2376.81
245 | 3 | 170 | 1304.1
246 | 4 | 328 | 2523.24
247 | 3 | 170 | 1304.1
248 | 1 | 35 | 274.05
249 | 1 | 42 | 328.86
251 | 1 | 132 | 1056
253 | 1 | 131 | 1048
301 | 2 | 142 | 1133.79
302 | 3 | 176 | 1351.08
303 | 3 | 206 | 1635.08
304 | 3 | 175 | 1343.25
305 | 3 | 249 | 1922.67
306 | 3 | 249 | 1922.67
307 | 3 | 249 | 1922.67
308 | 3 | 249 | 1922.67
309 | 3 | 249 | 1922.67
310 | 3 | 249 | 1922.67
311 | 3 | 249 | 1922.67
312 | 3 | 249 | 1922.67
313 | 3 | 249 | 1922.67
314 | 3 | 249 | 1922.67
315 | 3 | 249 | 1922.67
316 | 3 | 299 | 2314.17
317 | 3 | 249 | 1922.67
318 | 1 | 44 | 352
319 | 3 | 346 | 2685.18
320 | 1 | 95 | 760
321 | 3 | 301 | 2329.83
322 | 6 | 1049 | 9353.71
323 | 4 | 342 | 2650.86
325 | 3 | 158 | 1210.14
327 | 4 | 499 | 3885.17
328 | 3 | 209 | 1648.8
329 | 3 | 299 | 2319.17
330 | 3 | 175 | 1335.25
331 | 3 | 253 | 1953.99
332 | 3 | 249 | 1922.67
333 | 3 | 249 | 1922.67
334 | 3 | 249 | 1922.67
335 | 3 | 249 | 1922.67
336 | 3 | 249 | 1922.67
337 | 3 | 249 | 1922.67
338 | 3 | 249 | 1922.67
339 | 3 | 249 | 1922.67
340 | 3 | 249 | 1922.67
341 | 3 | 249 | 1922.67
342 | 3 | 249 | 1922.67
343 | 3 | 171 | 1311.93
344 | 3 | 307 | 2376.81
345 | 3 | 170 | 1304.1
346 | 4 | 328 | 2523.24
347 | 3 | 170 | 1304.1
348 | 1 | 35 | 274.05
349 | 1 | 42 | 328.86
351 | 1 | 132 | 1056
353 | 1 | 131 | 1048
401 | 2 | 168 | 1337.37
402 | 3 | 176 | 1351.08
403 | 4 | 238 | 1863.54
404 | 3 | 175 | 1343.25
405 | 3 | 249 | 1922.67
406 | 3 | 249 | 1922.67
407 | 3 | 249 | 1922.67
408 | 3 | 249 | 1922.67
409 | 3 | 249 | 1922.67
410 | 3 | 249 | 1922.67
411 | 3 | 249 | 1922.67
412 | 3 | 249 | 1922.67
413 | 3 | 249 | 1922.67
414 | 3 | 249 | 1922.67
415 | 3 | 249 | 1922.67
416 | 3 | 299 | 2314.17
417 | 3 | 249 | 1922.67
418 | 1 | 44 | 352
419 | 3 | 346 | 2685.18
420 | 1 | 95 | 760
421 | 3 | 301 | 2329.83
422 | 6 | 1156 | 10400.26
423 | 4 | 342 | 2650.86
424 | 1 | 175 | 1370.25
425 | 3 | 158 | 1210.14
427 | 4 | 499 | 3885.17
428 | 3 | 209 | 1648.8
429 | 3 | 299 | 2319.17
430 | 3 | 179 | 1366.57
431 | 3 | 253 | 1953.99
432 | 3 | 249 | 1922.67
433 | 3 | 249 | 1922.67
434 | 3 | 249 | 1922.67
435 | 3 | 249 | 1922.67
436 | 3 | 249 | 1922.67
437 | 3 | 249 | 1922.67
438 | 3 | 249 | 1922.67
439 | 3 | 249 | 1922.67
440 | 3 | 249 | 1922.67
441 | 3 | 249 | 1922.67
442 | 3 | 249 | 1922.67
443 | 3 | 171 | 1311.93
444 | 3 | 307 | 2376.81
445 | 3 | 170 | 1304.1
446 | 4 | 328 | 2523.24
447 | 3 | 170 | 1304.1
448 | 1 | 35 | 274.05
449 | 1 | 42 | 328.86
451 | 1 | 119 | 952
453 | 1 | 143 | 1144
501 | 2 | 168 | 1337.37
502 | 3 | 176 | 1351.08
503 | 4 | 238 | 1863.54
504 | 3 | 175 | 1343.25
505 | 3 | 249 | 1922.67
506 | 3 | 249 | 1922.67
507 | 3 | 249 | 1922.67
508 | 3 | 249 | 1922.67
509 | 3 | 249 | 1922.67
510 | 3 | 249 | 1922.67
511 | 3 | 249 | 1922.67
512 | 3 | 249 | 1922.67
513 | 3 | 249 | 1922.67
514 | 3 | 249 | 1922.67
515 | 3 | 249 | 1922.67
516 | 3 | 299 | 2314.17
517 | 3 | 249 | 1922.67
518 | 1 | 44 | 352
519 | 3 | 346 | 2685.18
520 | 1 | 95 | 760
521 | 3 | 301 | 2329.83
522 | 5 | 874 | 7983.46
523 | 4 | 342 | 2650.86
524 | 4 | 154 | 0
525 | 3 | 158 | 1210.14
527 | 4 | 499 | 3885.17
528 | 3 | 209 | 1648.8
529 | 3 | 299 | 2319.17
530 | 3 | 179 | 1366.57
531 | 3 | 253 | 1953.99
532 | 3 | 249 | 1922.67
533 | 3 | 249 | 1922.67
534 | 3 | 249 | 1922.67
535 | 3 | 249 | 1922.67
536 | 3 | 249 | 1922.67
537 | 3 | 249 | 1922.67
538 | 3 | 249 | 1922.67
539 | 3 | 249 | 1922.67
540 | 3 | 249 | 1922.67
541 | 3 | 249 | 1922.67
542 | 3 | 249 | 1922.67
543 | 3 | 171 | 1311.93
544 | 3 | 307 | 2376.81
545 | 3 | 170 | 1304.1
546 | 4 | 328 | 2523.24
547 | 3 | 170 | 1304.1
548 | 1 | 35 | 274.05
549 | 1 | 42 | 328.86
551 | 1 | 119 | 952
553 | 1 | 143 | 1144
601 | 2 | 168 | 1337.37
602 | 3 | 176 | 1351.08
603 | 4 | 238 | 1863.54
604 | 3 | 175 | 1343.25
605 | 3 | 249 | 1922.67
606 | 3 | 249 | 1922.67
607 | 3 | 249 | 1922.67
608 | 3 | 249 | 1922.67
609 | 3 | 249 | 1922.67
610 | 3 | 249 | 1922.67
611 | 3 | 249 | 1922.67
612 | 3 | 249 | 1922.67
613 | 3 | 249 | 1922.67
614 | 3 | 249 | 1922.67
615 | 3 | 249 | 1922.67
616 | 3 | 299 | 2314.17
617 | 3 | 249 | 1922.67
618 | 1 | 44 | 352
619 | 3 | 346 | 2685.18
620 | 1 | 95 | 760
621 | 3 | 301 | 2329.83
622 | 6 | 1156 | 10400.26
623 | 4 | 342 | 2650.86
624 | 4 | 154 | 0
625 | 3 | 158 | 1210.14
627 | 4 | 499 | 3885.17
628 | 3 | 209 | 1648.8
629 | 3 | 299 | 2319.17
630 | 3 | 179 | 1366.57
631 | 3 | 253 | 1953.99
632 | 3 | 249 | 1922.67
633 | 3 | 249 | 1922.67
634 | 3 | 249 | 1922.67
635 | 3 | 249 | 1922.67
636 | 3 | 249 | 1922.67
637 | 3 | 249 | 1922.67
638 | 3 | 249 | 1922.67
639 | 3 | 249 | 1922.67
640 | 3 | 249 | 1922.67
641 | 3 | 249 | 1922.67
642 | 3 | 249 | 1922.67
643 | 3 | 171 | 1311.93
644 | 3 | 307 | 2376.81
645 | 3 | 170 | 1304.1
646 | 4 | 328 | 2523.24
647 | 3 | 170 | 1304.1
648 | 1 | 35 | 274.05
649 | 1 | 42 | 328.86
651 | 1 | 119 | 952
653 | 1 | 143 | 1144
701 | 2 | 168 | 1337.37
702 | 3 | 176 | 1351.08
703 | 4 | 238 | 1863.54
704 | 3 | 175 | 1343.25
705 | 3 | 249 | 1922.67
706 | 3 | 249 | 1922.67
707 | 3 | 249 | 1922.67
708 | 3 | 249 | 1922.67
709 | 3 | 249 | 1922.67
710 | 3 | 249 | 1922.67
711 | 3 | 249 | 1922.67
712 | 3 | 249 | 1922.67
713 | 3 | 249 | 1922.67
714 | 3 | 249 | 1922.67
715 | 3 | 249 | 1922.67
716 | 3 | 299 | 2314.17
717 | 3 | 249 | 1922.67
718 | 1 | 44 | 352
719 | 3 | 346 | 2685.18
720 | 1 | 95 | 760
721 | 3 | 301 | 2329.83
722 | 5 | 874 | 7983.46
723 | 4 | 342 | 2650.86
724 | 2 | 172 | 1346.76
725 | 3 | 158 | 1210.14
727 | 4 | 499 | 3885.17
728 | 3 | 209 | 1648.8
729 | 3 | 299 | 2319.17
730 | 3 | 179 | 1366.57
731 | 3 | 253 | 1953.99
732 | 3 | 249 | 1922.67
733 | 3 | 249 | 1922.67
734 | 3 | 249 | 1922.67
735 | 3 | 249 | 1922.67
736 | 3 | 249 | 1922.67
737 | 3 | 249 | 1922.67
738 | 3 | 249 | 1922.67
739 | 3 | 249 | 1922.67
740 | 3 | 249 | 1922.67
741 | 3 | 249 | 1922.67
742 | 3 | 249 | 1922.67
743 | 3 | 171 | 1311.93
744 | 3 | 307 | 2376.81
745 | 3 | 170 | 1304.1
746 | 4 | 328 | 2523.24
747 | 3 | 170 | 1304.1
748 | 1 | 35 | 274.05
749 | 1 | 42 | 328.86
751 | 1 | 119 | 952
753 | 1 | 143 | 1144
801 | 1 | 179 | 1432
803 | 1 | 146 | 1245.38
824 | 1 | 265 | 2165.05
827 | 1 | 110 | 888.8
851 | 1 | 119 | 961.52
853 | 1 | 143 | 1144
101 Hall | 1 | 59 | 472
102 Hall | 1 | 478 | 4421.5
108 Hall | 1 | 73 | 492.75
131 Hall | 1 | 68 | 532.44
134 Hall | 1 | 96 | 751.68
20 Hall | 1 | 138 | 1080.54
202 Hall | 1 | 861 | 6741.63
225 Hall | 1 | 97 | 759.51
246 Hall | 1 | 692 | 5418.36
30 Hall | 1 | 233 | 1824.39
302 Hall | 1 | 861 | 6741.63
325 Hall | 1 | 97 | 759.51
346 Hall | 1 | 692 | 5418.36
40 Hall | 1 | 109 | 962.47
402 Hall | 1 | 840 | 6577.2
425 Hall | 1 | 97 | 759.51
446 Hall | 1 | 692 | 5418.36
46 Hall | 1 | 828 | 16560
502 Hall | 1 | 840 | 6577.2
525 Hall | 1 | 97 | 759.51
546 Hall | 1 | 692 | 5418.36
602 Hall | 1 | 840 | 6577.2
625 Hall | 1 | 97 | 759.51
646 Hall | 1 | 692 | 5418.36
702 Hall | 1 | 840 | 6577.2
725 Hall | 1 | 97 | 759.51
746 Hall | 1 | 692 | 5418.36
Grand Total | 1003 | 103737 | 868595.63

## Barnhart_79.pdf
PIVOT
[6 empty] | Calculated | Calculated |  |  |  |  | ft2 | ft3
RM. | USAGE | L | W | H | SQ.FT. | A | Volume | Mod room |  | Row Labels | Count of Mod room | Sum of SQ.FT. | Sum of Volume
1 | Stair | 20.48 | 7.92 | 10 | 110 | 162.2016 | 1100 | 1 | 1 | 1 | 2 | 131 | 1310
1 | Storage | 5.52 | 3.77 | 10 | 21 | 20.8104 | 210 | 1 | 2 | 3 | 2 | 131 | 1310
3 | Stair | 20.48 | 7.92 | 10 | 110 | 162.2016 | 1100 | 3 | 3 | 10 | 2 | 630 | 6507.9
3 | Storage | 5.52 | 3.77 | 10 | 21 | 20.8104 | 210 | 3 | 4 | 20 | 1 | 722 | 12996
10 | Mainance Shop | 30.28 | 19.89 | 10.33 | 431 | 602.2692 | 4452.23 | 10 | 5 | 21 | 2 | 916 | 16488
10 | Pump Room | 17.57 | 11.33 | 10.33 | 199 | 199.0681 | 2055.67 | 10 | 6 | 22 | 3 | 908 | 7584.05
20 | Hall | 16.83 | 8.19 | 7.83 | 138 | 137.8377 | 1080.54 | 20 Hall | 7 | 23 | 1 | 35 | 274.05
20 | Living Room | 32.35 | 22.35 | 18 | 722 | 723.0225 | 12996 | 20 | 8 | 24 | 1 | 42 | 433.86
21 | Janitor | 4.83 | 1.98 | 18 | 10 | 9.5634 | 180 | 21 | 9 | 25 | 2 | 184 | 1472
21 | Living Room | 42.75 | 25.09 | 18 | 906 | 1072.5975 | 16308 | 21 | 10 | 26 | 1 | 295 | 2336.4
22 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 22 | 11 | 28 | 1 | 171 | 1368
22 | Entrance Lobby | 44.44 | 22.04 | 8 | 710 | 979.4576 | 5680 | 22 | 12 | 29 | 2 | 80 | 640
22 | Stair | 21.02 | 8.19 | 10 | 163 | 172.1538 | 1630 | 22 | 13 | 30 | 1 | 315 | 2781.45
23 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 23 | 14 | 32 | 1 | 574 | 5068.42
24 | Foyer | 7.68 | 5.44 | 10.33 | 42 | 41.7792 | 433.86 | 24 | 15 | 40 | 1 | 893 | 9224.69
25 | Office | 16.54 | 14.54 | 8 | 170 | 240.4916 | 1360 | 25 | 16 | 41 | 4 | 591 | 4722.6
25 | Storage | 5.52 | 2.5 | 8 | 14 | 13.8 | 112 | 25 | 17 | 42 | 1 | 78 | 688.74
26 | Office | 27.14 | 13.71 | 7.92 | 295 | 372.0894 | 2336.4 | 26 | 18 | 43 | 1 | 266 | 2128
28 | Front Desk | 29 | 6.81 | 8 | 171 | 197.49 | 1368 | 28 | 19 | 44 | 1 | 103 | 909.49
29 | Electrical | 12.29 | 7.6 | 8 | 65 | 93.404 | 520 | 29 | 20 | 45 | 6 | 469 | 3752
29 | Vestibule | 4.04 | 3.83 | 8 | 15 | 15.4732 | 120 | 29 | 21 | 46 | 3 | 1541 | 29266
30 | Dishwashing | 19.27 | 18.08 | 8.83 | 315 | 348.4016 | 2781.45 | 30 | 22 | 47 | 1 | 140 | 2800
30 | Hall | 19.12 | 16.02 | 7.83 | 233 | 306.3024 | 1824.39 | 30 Hall | 23 | 51 | 1 | 115 | 1150
32 | Serving Bar | 32.46 | 22.89 | 8.83 | 574 | 743.0094 | 5068.42 | 32 | 24 | 53 | 1 | 115 | 1150
40 | Hall | 24.04 | 4.62 | 8.83 | 109 | 111.0648 | 962.47 | 40 Hall | 25 | 101 | 5 | 422 | 3644.89
40 | Kitchen | 37.62 | 24.27 | 10.33 | 893 | 913.0374 | 9224.69 | 40 | 26 | 102 | 1 | 264 | 2442
41 | Freezer | 14.73 | 8.77 | 7 | 129 | 129.1821 | 903 | 41 | 27 | 103 | 1 | 129 | 1032
41 | Refrigerator | 9.74 | 7.32 | 7 | 71 | 71.2968 | 497 | 41 | 28 | 105 | 4 | 230 | 2050.8
41 | Refrigerator | 9.74 | 7.32 | 7 | 71 | 71.2968 | 497 | 41 | 29 | 106 | 3 | 222 | 2053.5
41 | Storage | 19.87 | 16.21 | 8.83 | 320 | 322.0927 | 2825.6 | 41 | 30 | 107 | 3 | 249 | 1922.67
42 | Office | 11.5 | 6.84 | 8.83 | 78 | 78.66 | 688.74 | 42 | 31 | 108 | 3 | 255 | 2358.75
43 | Loading | 16.42 | 16.33 | 8 | 266 | 268.1386 | 2128 | 43 | 32 | 109 | 3 | 249 | 1922.67
44 | Mechanical | 11.5 | 8.96 | 8.83 | 103 | 103.04 | 909.49 | 44 | 33 | 110 | 3 | 249 | 1922.67
45 | Janitor | 5.1 | 4.06 | 8 | 21 | 20.706 | 168 | 45 | 34 | 111 | 3 | 249 | 1922.67
45 | Restroom | 11.98 | 4.77 | 8 | 53 | 57.1446 | 424 | 45 | 35 | 112 | 3 | 249 | 1922.67
45 | Restroom | 6.46 | 4.06 | 8 | 26 | 26.2276 | 208 | 45 | 36 | 113 | 3 | 249 | 1922.67
45 | Service | 14.87 | 12.69 | 8 | 185 | 188.7003 | 1480 | 45 | 37 | 114 | 3 | 249 | 1922.67
45 | Trash Room | 22.49 | 8.21 | 8 | 130 | 184.6429 | 1040 | 45 | 38 | 115 | 3 | 249 | 1922.67
45 | Vestibule | 9.29 | 5.85 | 8 | 54 | 54.3465 | 432 | 45 | 39 | 116 | 3 | 299 | 2314.17
46 | Dining | 50.34 | 36.24 | 20 | 1400 | 1824.3216 | 28000 | 46 | 40 | 117 | 3 | 249 | 1922.67
46 | Hall | 73.6 | 14.08 | 20 | 828 | 1036.288 | 16560 | 46 Hall | 41 | 118 | 1 | 44 | 352
46 | Stair | 19.65 | 5.46 | 10 | 93 | 107.289 | 930 | 46 | 42 | 119 | 3 | 249 | 1922.67
46 | Storage | 11.06 | 5.46 | 7 | 48 | 60.3876 | 336 | 46 | 43 | 120 | 1 | 62 | 573.5
47 | Storage | 24.44 | 11.46 | 20 | 140 | 280.0824 | 2800 | 47 | 44 | 121 | 1 | 57 | 527.25
51 | Stair | 16.33 | 8 | 10 | 115 | 130.64 | 1150 | 51 | 45 | 122 | 5 | 1511 | 13559.69
53 | Stair | 16.33 | 8 | 10 | 115 | 130.64 | 1150 | 53 | 46 | 123 | 1 | 35 | 274.05
101 | Apt Kitchen | 12.21 | 11.82 | 9.25 | 116 | 144.3222 | 1073 | 101 | 47 | 128 | 2 | 137 | 1085.04
101 | Apt Study | 15.83 | 8.46 | 9.25 | 130 | 133.9218 | 1202.5 | 101 | 48 | 129 | 1 | 9 | 70.47
101 | Apt Toilet/Shower | 7.75 | 5.25 | 6.83 | 33 | 40.6875 | 225.39 | 101 | 49 | 130 | 1 | 35 | 274.05
101 | Hall | 12.87 | 5.97 | 8 | 59 | 76.8339 | 472 | 101 Hall | 50 | 131 | 1 | 105 | 822.15
101 | Stair | 16.33 | 7.93 | 8 | 129 | 129.4969 | 1032 | 101 | 51 | 132 | 1 | 15 | 117.45
101 | Vestibule | 4.06 | 3.48 | 8 | 14 | 14.1288 | 112 | 101 | 52 | 133 | 2 | 82 | 642.06
102 | Apt Living | 18.3 | 14 | 9.25 | 264 | 256.2 | 2442 | 102 | 53 | 134 | 1 | 49 | 383.67
102 | Hall | 97.85 | 6.46 | 9.25 | 478 | 632.111 | 4421.5 | 102 Hall | 54 | 135 | 1 | 100 | 783
103 | Stair | 16.33 | 7.93 | 8 | 129 | 129.4969 | 1032 | 103 | 55 | 136 | 2 | 1600 | 12528
105 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 105 | 56 | 146 | 1 | 83 | 830
105 | Storage | 6.19 | 4.94 | 9.25 | 31 | 30.5786 | 286.75 | 105 | 57 | 151 | 1 | 131 | 1048
105 | Student Room | 21.27 | 11.94 | 9.25 | 164 | 253.9638 | 1517 | 105 | 58 | 153 | 1 | 131 | 1048
105 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 105 | 59 | 201 | 2 | 142 | 1133.79
106 | Apt Bedroom | 22.36 | 11.95 | 9.25 | 170 | 267.202 | 1572.5 | 106 | 60 | 202 | 3 | 176 | 1351.08
106 | Apt Closet | 7.78 | 4.6 | 9.25 | 26 | 35.788 | 240.5 | 106 | 61 | 203 | 3 | 206 | 1635.08
106 | Apt Toilet/Shower | 8.58 | 3.98 | 9.25 | 26 | 34.1484 | 240.5 | 106 | 62 | 204 | 3 | 175 | 1343.25
107 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 107 | 63 | 205 | 3 | 249 | 1922.67
107 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 107 | 64 | 206 | 3 | 249 | 1922.67
107 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 107 | 65 | 207 | 3 | 249 | 1922.67
108 | Apt Bedroom | 22.35 | 11.94 | 9.25 | 197 | 266.859 | 1822.25 | 108 | 66 | 208 | 3 | 249 | 1922.67
108 | Apt Closet | 7.85 | 2.17 | 9.25 | 16 | 17.0345 | 148 | 108 | 67 | 209 | 3 | 249 | 1922.67
108 | Apt Toilet/Bath | 7.85 | 5.37 | 9.25 | 42 | 42.1545 | 388.5 | 108 | 68 | 210 | 3 | 249 | 1922.67
108 | Hall | 12.02 | 10.49 | 6.75 | 73 | 126.0898 | 492.75 | 108 Hall | 69 | 211 | 3 | 249 | 1922.67
109 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 109 | 70 | 212 | 3 | 249 | 1922.67
109 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 109 | 71 | 213 | 3 | 249 | 1922.67
109 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 109 | 72 | 214 | 3 | 249 | 1922.67
110 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 110 | 73 | 215 | 3 | 249 | 1922.67
110 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 110 | 74 | 216 | 3 | 299 | 2314.17
110 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 110 | 75 | 217 | 3 | 249 | 1922.67
111 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 111 | 76 | 218 | 1 | 44 | 352
111 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 111 | 77 | 219 | 3 | 346 | 2685.18
111 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 111 | 78 | 220 | 1 | 95 | 760
112 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 112 | 79 | 221 | 3 | 301 | 2329.83
112 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 112 | 80 | 222 | 7 | 1331 | 11770.51
112 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 112 | 81 | 223 | 4 | 342 | 2650.86
113 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 113 | 82 | 225 | 3 | 158 | 1210.14
113 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 113 | 83 | 227 | 4 | 499 | 3885.17
113 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 113 | 84 | 228 | 3 | 209 | 1648.8
114 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 114 | 85 | 229 | 3 | 299 | 2319.17
114 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 114 | 86 | 230 | 3 | 179 | 1366.57
114 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 114 | 87 | 231 | 3 | 253 | 1953.99
115 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 115 | 88 | 232 | 3 | 249 | 1922.67
115 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 115 | 89 | 233 | 3 | 249 | 1922.67
115 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 115 | 90 | 234 | 3 | 249 | 1922.67
116 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 116 | 91 | 235 | 3 | 249 | 1922.67
116 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 116 | 92 | 236 | 3 | 249 | 1922.67
116 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 116 | 93 | 237 | 3 | 249 | 1922.67
117 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 117 | 94 | 238 | 3 | 249 | 1922.67
117 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 117 | 95 | 239 | 3 | 249 | 1922.67
117 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 117 | 96 | 240 | 3 | 249 | 1922.67
118 | Tub Room | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 118 | 97 | 241 | 3 | 249 | 1922.67
119 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 119 | 98 | 242 | 3 | 249 | 1922.67
119 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 119 | 99 | 243 | 3 | 171 | 1311.93
119 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 119 | 100 | 244 | 3 | 307 | 2376.81
120 | Laundry Room | 7.92 | 7.83 | 9.25 | 62 | 62.0136 | 573.5 | 120 | 101 | 245 | 3 | 170 | 1304.1
121 | Mechanical | 8.04 | 7.5 | 9.25 | 57 | 60.3 | 527.25 | 121 | 102 | 246 | 4 | 328 | 2523.24
122 | Balcony | 12.5 | 6.46 | 7.83 | 58 | 80.75 | 454.14 | 122 | 103 | 247 | 3 | 170 | 1304.1
122 | Comp.Terminal | 5.76 | 5.74 | 9.25 | 27 | 33.0624 | 249.75 | 122 | 104 | 248 | 1 | 35 | 274.05
122 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 122 | 105 | 249 | 1 | 42 | 328.86
122 | Lobby | 43.5 | 41.58 | 9.25 | 1163 | 1808.73 | 10757.75 | 122 | 106 | 251 | 1 | 132 | 1056
122 | Stair | 28.96 | 8.19 | 8 | 228 | 237.1824 | 1824 | 122 | 107 | 253 | 1 | 131 | 1048
123 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 123 | 108 | 301 | 2 | 142 | 1133.79
128 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 128 | 109 | 302 | 3 | 176 | 1351.08
128 | Janitor | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 128 | 110 | 303 | 3 | 206 | 1635.08
129 | Trash Chute | 6.19 | 1.42 | 7.83 | 9 | 8.7898 | 70.47 | 129 | 111 | 304 | 3 | 175 | 1343.25
130 | Office | 7.6 | 4.6 | 7.83 | 35 | 34.96 | 274.05 | 130 | 112 | 305 | 3 | 249 | 1922.67
131 | Hall | 12.99 | 7.19 | 7.83 | 68 | 93.3981 | 532.44 | 131 Hall | 113 | 306 | 3 | 249 | 1922.67
131 | Storage | 11.58 | 9.08 | 7.83 | 105 | 105.1464 | 822.15 | 131 | 114 | 307 | 3 | 249 | 1922.67
132 | Janitor | 5.94 | 2.5 | 7.83 | 15 | 14.85 | 117.45 | 132 | 115 | 308 | 3 | 249 | 1922.67
133 | Janitor Supplies | 11.44 | 5.94 | 7.83 | 64 | 67.9536 | 501.12 | 133 | 116 | 309 | 3 | 249 | 1922.67
133 | Vestibule | 5.94 | 3 | 7.83 | 18 | 17.82 | 140.94 | 133 | 117 | 310 | 3 | 249 | 1922.67
134 | Hall | 20.33 | 5.65 | 7.83 | 96 | 114.8645 | 751.68 | 134 Hall | 118 | 311 | 3 | 249 | 1922.67
134 | Storage | 12 | 5 | 7.83 | 49 | 60 | 383.67 | 134 | 119 | 312 | 3 | 249 | 1922.67
135 | Mechanical | 12.87 | 7.83 | 7.83 | 100 | 100.7721 | 783 | 135 | 120 | 313 | 3 | 249 | 1922.67
136 | Lounge | 48.52 | 35.54 | 7.83 | 1355 | 1724.4008 | 10609.65 | 136 | 121 | 314 | 3 | 249 | 1922.67
136 | Storage | 17.37 | 14.77 | 7.83 | 245 | 256.5549 | 1918.35 | 136 | 122 | 315 | 3 | 249 | 1922.67
146 | Stair | 12.69 | 10.96 | 10 | 83 | 139.0824 | 830 | 146 | 123 | 316 | 3 | 299 | 2314.17
151 | Stair | 16.33 | 8 | 8 | 131 | 130.64 | 1048 | 151 | 124 | 317 | 3 | 249 | 1922.67
153 | Stair | 16.33 | 8 | 8 | 131 | 130.64 | 1048 | 153 | 125 | 318 | 1 | 44 | 352
201 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 201 | 126 | 319 | 3 | 346 | 2685.18
201 | Vestibule | 3.67 | 3.48 | 7.83 | 13 | 12.7716 | 101.79 | 201 | 127 | 320 | 1 | 95 | 760
202 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 202 | 128 | 321 | 3 | 301 | 2329.83
202 | Hall | 120.35 | 14.76 | 7.83 | 861 | 1776.366 | 6741.63 | 202 Hall | 129 | 322 | 6 | 1049 | 9353.71
202 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 202 | 130 | 323 | 4 | 342 | 2650.86
202 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 202 | 131 | 325 | 3 | 158 | 1210.14
203 | Stair | 16.33 | 7.94 | 8 | 130 | 129.6602 | 1040 | 203 | 132 | 327 | 4 | 499 | 3885.17
203 | Study | 6.5 | 6.1 | 7.83 | 40 | 39.65 | 313.2 | 203 | 133 | 328 | 3 | 209 | 1648.8
203 | Study | 6.69 | 5.37 | 7.83 | 36 | 35.9253 | 281.88 | 203 | 134 | 329 | 3 | 299 | 2319.17
204 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 204 | 135 | 330 | 3 | 175 | 1335.25
204 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 204 | 136 | 331 | 3 | 253 | 1953.99
204 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 204 | 137 | 332 | 3 | 249 | 1922.67
205 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 205 | 138 | 333 | 3 | 249 | 1922.67
205 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 205 | 139 | 334 | 3 | 249 | 1922.67
205 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 205 | 140 | 335 | 3 | 249 | 1922.67
206 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 206 | 141 | 336 | 3 | 249 | 1922.67
206 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 206 | 142 | 337 | 3 | 249 | 1922.67
206 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 206 | 143 | 338 | 3 | 249 | 1922.67
207 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 207 | 144 | 339 | 3 | 249 | 1922.67
207 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 207 | 145 | 340 | 3 | 249 | 1922.67
207 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 207 | 146 | 341 | 3 | 249 | 1922.67
208 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 208 | 147 | 342 | 3 | 249 | 1922.67
208 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 208 | 148 | 343 | 3 | 171 | 1311.93
208 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 208 | 149 | 344 | 3 | 307 | 2376.81
209 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 209 | 150 | 345 | 3 | 170 | 1304.1
209 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 209 | 151 | 346 | 4 | 328 | 2523.24
209 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 209 | 152 | 347 | 3 | 170 | 1304.1
210 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 210 | 153 | 348 | 1 | 35 | 274.05
210 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 210 | 154 | 349 | 1 | 42 | 328.86
210 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 210 | 155 | 351 | 1 | 132 | 1056
211 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 211 | 156 | 353 | 1 | 131 | 1048
211 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 211 | 157 | 401 | 2 | 168 | 1337.37
211 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 211 | 158 | 402 | 3 | 176 | 1351.08
212 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 212 | 159 | 403 | 4 | 238 | 1863.54
212 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 212 | 160 | 404 | 3 | 175 | 1343.25
212 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 212 | 161 | 405 | 3 | 249 | 1922.67
213 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 213 | 162 | 406 | 3 | 249 | 1922.67
213 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 213 | 163 | 407 | 3 | 249 | 1922.67
213 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 213 | 164 | 408 | 3 | 249 | 1922.67
214 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 214 | 165 | 409 | 3 | 249 | 1922.67
214 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 214 | 166 | 410 | 3 | 249 | 1922.67
214 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 214 | 167 | 411 | 3 | 249 | 1922.67
215 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 215 | 168 | 412 | 3 | 249 | 1922.67
215 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 215 | 169 | 413 | 3 | 249 | 1922.67
215 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 215 | 170 | 414 | 3 | 249 | 1922.67
216 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 216 | 171 | 415 | 3 | 249 | 1922.67
216 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 216 | 172 | 416 | 3 | 299 | 2314.17
216 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 216 | 173 | 417 | 3 | 249 | 1922.67
217 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 217 | 174 | 418 | 1 | 44 | 352
217 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 217 | 175 | 419 | 3 | 346 | 2685.18
217 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 217 | 176 | 420 | 1 | 95 | 760
218 | Tub Room | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 218 | 177 | 421 | 3 | 301 | 2329.83
219 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 219 | 178 | 422 | 6 | 1156 | 10400.26
219 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 219 | 179 | 423 | 4 | 342 | 2650.86
219 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 219 | 180 | 424 | 1 | 175 | 1370.25
220 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 220 | 181 | 425 | 3 | 158 | 1210.14
221 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 221 | 182 | 427 | 4 | 499 | 3885.17
221 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 221 | 183 | 428 | 3 | 209 | 1648.8
221 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 221 | 184 | 429 | 3 | 299 | 2319.17
222 | Conference | 14.62 | 10.12 | 7.83 | 135 | 147.9544 | 1057.05 | 222 | 185 | 430 | 3 | 179 | 1366.57
222 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 222 | 186 | 431 | 3 | 253 | 1953.99
222 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 222 | 187 | 432 | 3 | 249 | 1922.67
222 | Lobby | 43.48 | 38.12 | 9.25 | 955 | 1657.4576 | 8833.75 | 222 | 188 | 433 | 3 | 249 | 1922.67
222 | Stair | 22.46 | 8.19 | 7.83 | 175 | 183.9474 | 1370.25 | 222 | 189 | 434 | 3 | 249 | 1922.67
222 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 222 | 190 | 435 | 3 | 249 | 1922.67
222 | Trash chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 222 | 191 | 436 | 3 | 249 | 1922.67
223 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 223 | 192 | 437 | 3 | 249 | 1922.67
223 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 223 | 193 | 438 | 3 | 249 | 1922.67
223 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 223 | 194 | 439 | 3 | 249 | 1922.67
223 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 223 | 195 | 440 | 3 | 249 | 1922.67
225 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 225 | 196 | 441 | 3 | 249 | 1922.67
225 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 225 Hall | 197 | 442 | 3 | 249 | 1922.67
225 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 225 | 198 | 443 | 3 | 171 | 1311.93
225 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 225 | 199 | 444 | 3 | 307 | 2376.81
227 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 227 | 200 | 445 | 3 | 170 | 1304.1
227 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 227 | 201 | 446 | 4 | 328 | 2523.24
227 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 227 | 202 | 447 | 3 | 170 | 1304.1
227 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 227 | 203 | 448 | 1 | 35 | 274.05
228 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 228 | 204 | 449 | 1 | 42 | 328.86
228 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 228 | 205 | 451 | 1 | 119 | 952
228 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 228 | 206 | 453 | 1 | 143 | 1144
229 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 229 | 207 | 501 | 2 | 168 | 1337.37
229 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 229 | 208 | 502 | 3 | 176 | 1351.08
229 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 229 | 209 | 503 | 4 | 238 | 1863.54
230 | Closet | 4.35 | 1.89 | 6.83 | 8 | 8.2215 | 54.64 | 230 | 210 | 504 | 3 | 175 | 1343.25
230 | Student Room | 17.69 | 12.13 | 7.83 | 144 | 214.5797 | 1127.52 | 230 | 211 | 505 | 3 | 249 | 1922.67
230 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 230 | 212 | 506 | 3 | 249 | 1922.67
231 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 231 | 213 | 507 | 3 | 249 | 1922.67
231 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 231 | 214 | 508 | 3 | 249 | 1922.67
231 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 231 | 215 | 509 | 3 | 249 | 1922.67
232 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 232 | 216 | 510 | 3 | 249 | 1922.67
232 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 232 | 217 | 511 | 3 | 249 | 1922.67
232 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 232 | 218 | 512 | 3 | 249 | 1922.67
233 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 233 | 219 | 513 | 3 | 249 | 1922.67
233 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 233 | 220 | 514 | 3 | 249 | 1922.67
233 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 233 | 221 | 515 | 3 | 249 | 1922.67
234 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 234 | 222 | 516 | 3 | 299 | 2314.17
234 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 234 | 223 | 517 | 3 | 249 | 1922.67
234 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 234 | 224 | 518 | 1 | 44 | 352
235 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 235 | 225 | 519 | 3 | 346 | 2685.18
235 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 235 | 226 | 520 | 1 | 95 | 760
235 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 235 | 227 | 521 | 3 | 301 | 2329.83
236 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 236 | 228 | 522 | 5 | 874 | 7983.46
236 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 236 | 229 | 523 | 4 | 342 | 2650.86
236 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 236 | 230 | 524 | 4 | 154 | 0
237 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 237 | 231 | 525 | 3 | 158 | 1210.14
237 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 237 | 232 | 527 | 4 | 499 | 3885.17
237 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 237 | 233 | 528 | 3 | 209 | 1648.8
238 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 238 | 234 | 529 | 3 | 299 | 2319.17
238 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 238 | 235 | 530 | 3 | 179 | 1366.57
238 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 238 | 236 | 531 | 3 | 253 | 1953.99
239 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 239 | 237 | 532 | 3 | 249 | 1922.67
239 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 239 | 238 | 533 | 3 | 249 | 1922.67
239 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 239 | 239 | 534 | 3 | 249 | 1922.67
240 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 240 | 240 | 535 | 3 | 249 | 1922.67
240 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 240 | 241 | 536 | 3 | 249 | 1922.67
240 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 240 | 242 | 537 | 3 | 249 | 1922.67
241 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 241 | 243 | 538 | 3 | 249 | 1922.67
241 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 241 | 244 | 539 | 3 | 249 | 1922.67
241 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 241 | 245 | 540 | 3 | 249 | 1922.67
242 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 242 | 246 | 541 | 3 | 249 | 1922.67
242 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 242 | 247 | 542 | 3 | 249 | 1922.67
242 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 242 | 248 | 543 | 3 | 171 | 1311.93
243 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 243 | 249 | 544 | 3 | 307 | 2376.81
243 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 243 | 250 | 545 | 3 | 170 | 1304.1
243 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 243 | 251 | 546 | 4 | 328 | 2523.24
244 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 244 | 252 | 547 | 3 | 170 | 1304.1
244 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 244 | 253 | 548 | 1 | 35 | 274.05
244 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 244 | 254 | 549 | 1 | 42 | 328.86
245 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 245 | 255 | 551 | 1 | 119 | 952
245 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 245 | 256 | 553 | 1 | 143 | 1144
245 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 245 | 257 | 601 | 2 | 168 | 1337.37
246 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 246 | 258 | 602 | 3 | 176 | 1351.08
246 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 246 Hall | 259 | 603 | 4 | 238 | 1863.54
246 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 246 | 260 | 604 | 3 | 175 | 1343.25
246 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 246 | 261 | 605 | 3 | 249 | 1922.67
246 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 246 | 262 | 606 | 3 | 249 | 1922.67
247 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 247 | 263 | 607 | 3 | 249 | 1922.67
247 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 247 | 264 | 608 | 3 | 249 | 1922.67
247 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 247 | 265 | 609 | 3 | 249 | 1922.67
248 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 248 | 266 | 610 | 3 | 249 | 1922.67
249 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 249 | 267 | 611 | 3 | 249 | 1922.67
251 | Stair | 16.75 | 8 | 8 | 132 | 134 | 1056 | 251 | 268 | 612 | 3 | 249 | 1922.67
253 | Stair | 16.33 | 8 | 8 | 131 | 130.64 | 1048 | 253 | 269 | 613 | 3 | 249 | 1922.67
301 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 301 | 270 | 614 | 3 | 249 | 1922.67
301 | Vestibule | 3.67 | 3.48 | 7.83 | 13 | 12.7716 | 101.79 | 301 | 271 | 615 | 3 | 249 | 1922.67
302 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 302 | 272 | 616 | 3 | 299 | 2314.17
302 | Hall | 120.35 | 14.76 | 7.83 | 861 | 1776.366 | 6741.63 | 302 Hall | 273 | 617 | 3 | 249 | 1922.67
302 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 302 | 274 | 618 | 1 | 44 | 352
302 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 302 | 275 | 619 | 3 | 346 | 2685.18
303 | Stair | 16.33 | 7.94 | 8 | 130 | 129.6602 | 1040 | 303 | 276 | 620 | 1 | 95 | 760
303 | Study | 6.5 | 6.1 | 7.83 | 40 | 39.65 | 313.2 | 303 | 277 | 621 | 3 | 301 | 2329.83
303 | Study | 6.69 | 5.37 | 7.83 | 36 | 35.9253 | 281.88 | 303 | 278 | 622 | 6 | 1156 | 10400.26
304 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 304 | 279 | 623 | 4 | 342 | 2650.86
304 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 304 | 280 | 624 | 4 | 154 | 0
304 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 304 | 281 | 625 | 3 | 158 | 1210.14
305 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 305 | 282 | 627 | 4 | 499 | 3885.17
305 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 305 | 283 | 628 | 3 | 209 | 1648.8
305 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 305 | 284 | 629 | 3 | 299 | 2319.17
306 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 306 | 285 | 630 | 3 | 179 | 1366.57
306 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 306 | 286 | 631 | 3 | 253 | 1953.99
306 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 306 | 287 | 632 | 3 | 249 | 1922.67
307 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 307 | 288 | 633 | 3 | 249 | 1922.67
307 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 307 | 289 | 634 | 3 | 249 | 1922.67
307 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 307 | 290 | 635 | 3 | 249 | 1922.67
308 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 308 | 291 | 636 | 3 | 249 | 1922.67
308 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 308 | 292 | 637 | 3 | 249 | 1922.67
308 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 308 | 293 | 638 | 3 | 249 | 1922.67
309 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 309 | 294 | 639 | 3 | 249 | 1922.67
309 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 309 | 295 | 640 | 3 | 249 | 1922.67
309 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 309 | 296 | 641 | 3 | 249 | 1922.67
310 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 310 | 297 | 642 | 3 | 249 | 1922.67
310 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 310 | 298 | 643 | 3 | 171 | 1311.93
310 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 310 | 299 | 644 | 3 | 307 | 2376.81
311 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 311 | 300 | 645 | 3 | 170 | 1304.1
311 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 311 | 301 | 646 | 4 | 328 | 2523.24
311 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 311 | 302 | 647 | 3 | 170 | 1304.1
312 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 312 | 303 | 648 | 1 | 35 | 274.05
312 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 312 | 304 | 649 | 1 | 42 | 328.86
312 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 312 | 305 | 651 | 1 | 119 | 952
313 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 313 | 306 | 653 | 1 | 143 | 1144
313 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 313 | 307 | 701 | 2 | 168 | 1337.37
313 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 313 | 308 | 702 | 3 | 176 | 1351.08
314 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 314 | 309 | 703 | 4 | 238 | 1863.54
314 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 314 | 310 | 704 | 3 | 175 | 1343.25
314 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 314 | 311 | 705 | 3 | 249 | 1922.67
315 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 315 | 312 | 706 | 3 | 249 | 1922.67
315 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 315 | 313 | 707 | 3 | 249 | 1922.67
315 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 315 | 314 | 708 | 3 | 249 | 1922.67
316 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 316 | 315 | 709 | 3 | 249 | 1922.67
316 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 316 | 316 | 710 | 3 | 249 | 1922.67
316 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 316 | 317 | 711 | 3 | 249 | 1922.67
317 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 317 | 318 | 712 | 3 | 249 | 1922.67
317 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 317 | 319 | 713 | 3 | 249 | 1922.67
317 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 317 | 320 | 714 | 3 | 249 | 1922.67
318 | Tub Room | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 318 | 321 | 715 | 3 | 249 | 1922.67
319 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 319 | 322 | 716 | 3 | 299 | 2314.17
319 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 319 | 323 | 717 | 3 | 249 | 1922.67
319 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 319 | 324 | 718 | 1 | 44 | 352
320 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 320 | 325 | 719 | 3 | 346 | 2685.18
321 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 321 | 326 | 720 | 1 | 95 | 760
321 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 321 | 327 | 721 | 3 | 301 | 2329.83
321 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 321 | 328 | 722 | 5 | 874 | 7983.46
322 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 322 | 329 | 723 | 4 | 342 | 2650.86
322 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 322 | 330 | 724 | 2 | 172 | 1346.76
322 | Lobby | 43.48 | 38.12 | 9.25 | 808 | 1657.4576 | 7474 | 322 | 331 | 725 | 3 | 158 | 1210.14
322 | Stair | 22.46 | 8.19 | 7.83 | 175 | 183.9474 | 1370.25 | 322 | 332 | 727 | 4 | 499 | 3885.17
322 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 322 | 333 | 728 | 3 | 209 | 1648.8
322 | Trash Chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 322 | 334 | 729 | 3 | 299 | 2319.17
323 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 323 | 335 | 730 | 3 | 179 | 1366.57
323 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 323 | 336 | 731 | 3 | 253 | 1953.99
323 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 323 | 337 | 732 | 3 | 249 | 1922.67
323 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 323 | 338 | 733 | 3 | 249 | 1922.67
325 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 325 | 339 | 734 | 3 | 249 | 1922.67
325 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 325 Hall | 340 | 735 | 3 | 249 | 1922.67
325 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 325 | 341 | 736 | 3 | 249 | 1922.67
325 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 325 | 342 | 737 | 3 | 249 | 1922.67
327 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 327 | 343 | 738 | 3 | 249 | 1922.67
327 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 327 | 344 | 739 | 3 | 249 | 1922.67
327 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 327 | 345 | 740 | 3 | 249 | 1922.67
327 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 327 | 346 | 741 | 3 | 249 | 1922.67
328 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 328 | 347 | 742 | 3 | 249 | 1922.67
328 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 328 | 348 | 743 | 3 | 171 | 1311.93
328 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 328 | 349 | 744 | 3 | 307 | 2376.81
329 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 329 | 350 | 745 | 3 | 170 | 1304.1
329 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 329 | 351 | 746 | 4 | 328 | 2523.24
329 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 329 | 352 | 747 | 3 | 170 | 1304.1
330 | Closet | 4.35 | 1.89 | 6.83 | 8 | 8.2215 | 54.64 | 330 | 353 | 748 | 1 | 35 | 274.05
330 | Student Room | 17.69 | 12.13 | 7.83 | 140 | 214.5797 | 1096.2 | 330 | 354 | 749 | 1 | 42 | 328.86
330 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 330 | 355 | 751 | 1 | 119 | 952
331 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 331 | 356 | 753 | 1 | 143 | 1144
331 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 331 | 357 | 801 | 1 | 179 | 1432
331 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 331 | 358 | 803 | 1 | 146 | 1245.38
332 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 332 | 359 | 824 | 1 | 265 | 2165.05
332 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 332 | 360 | 827 | 1 | 110 | 888.8
332 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 332 | 361 | 851 | 1 | 119 | 961.52
333 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 333 | 362 | 853 | 1 | 143 | 1144
333 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 333 | 363 | 101 Hall | 1 | 59 | 472
333 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 333 | 364 | 102 Hall | 1 | 478 | 4421.5
334 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 334 | 365 | 108 Hall | 1 | 73 | 492.75
334 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 334 | 366 | 131 Hall | 1 | 68 | 532.44
334 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 334 | 367 | 134 Hall | 1 | 96 | 751.68
335 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 335 | 368 | 20 Hall | 1 | 138 | 1080.54
335 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 335 | 369 | 202 Hall | 1 | 861 | 6741.63
335 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 335 | 370 | 225 Hall | 1 | 97 | 759.51
336 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 336 | 371 | 246 Hall | 1 | 692 | 5418.36
336 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 336 | 372 | 30 Hall | 1 | 233 | 1824.39
336 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 336 | 373 | 302 Hall | 1 | 861 | 6741.63
337 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 337 | 374 | 325 Hall | 1 | 97 | 759.51
337 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 337 | 375 | 346 Hall | 1 | 692 | 5418.36
337 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 337 | 376 | 40 Hall | 1 | 109 | 962.47
338 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 338 | 377 | 402 Hall | 1 | 840 | 6577.2
338 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 338 | 378 | 425 Hall | 1 | 97 | 759.51
338 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 338 | 379 | 446 Hall | 1 | 692 | 5418.36
339 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 339 | 380 | 46 Hall | 1 | 828 | 16560
339 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 339 | 381 | 502 Hall | 1 | 840 | 6577.2
339 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 339 | 382 | 525 Hall | 1 | 97 | 759.51
340 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 340 | 383 | 546 Hall | 1 | 692 | 5418.36
340 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 340 | 384 | 602 Hall | 1 | 840 | 6577.2
340 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 340 | 385 | 625 Hall | 1 | 97 | 759.51
341 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 341 | 386 | 646 Hall | 1 | 692 | 5418.36
341 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 341 | 387 | 702 Hall | 1 | 840 | 6577.2
341 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 341 | 388 | 725 Hall | 1 | 97 | 759.51
342 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 342 | 389 | 746 Hall | 1 | 692 | 5418.36
342 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 342 | 390 | Grand Total | 1003 | 103737 | 868595.63
342 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 342 | 391
343 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 343 | 392
343 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 343 | 393
343 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 343 | 394
344 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 344 | 395
344 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 344 | 396
344 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 344 | 397
345 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 345 | 398
345 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 345 | 399
345 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 345 | 400
346 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 346 | 401
346 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 346 Hall | 402
346 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 346 | 403
346 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 346 | 404
346 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 346 | 405
347 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 347 | 406
347 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 347 | 407
347 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 347 | 408
348 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 348 | 409
349 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 349 | 410
351 | Stair | 16.75 | 8 | 8 | 132 | 134 | 1056 | 351 | 411
353 | Stair | 16.33 | 8 | 8 | 131 | 130.64 | 1048 | 353 | 412
401 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 401 | 413
401 | Vestibule | 11.08 | 3.48 | 7.83 | 39 | 38.5584 | 305.37 | 401 | 414
402 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 402 | 415
402 | Hall | 120.35 | 14.76 | 7.83 | 840 | 1776.366 | 6577.2 | 402 Hall | 416
402 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 402 | 417
402 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 402 | 418
403 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 403 | 419
403 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 403 | 420
403 | Student Room | 14.87 | 13.69 | 7.83 | 183 | 203.5703 | 1432.89 | 403 | 421
403 | Toilet/Shower | 7.94 | 3.92 | 7.83 | 27 | 31.1248 | 211.41 | 403 | 422
404 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 404 | 423
404 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 404 | 424
404 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 404 | 425
405 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 405 | 426
405 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 405 | 427
405 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 405 | 428
406 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 406 | 429
406 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 406 | 430
406 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 406 | 431
407 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 407 | 432
407 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 407 | 433
407 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 407 | 434
408 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 408 | 435
408 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 408 | 436
408 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 408 | 437
409 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 409 | 438
409 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 409 | 439
409 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 409 | 440
410 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 410 | 441
410 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 410 | 442
410 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 410 | 443
411 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 411 | 444
411 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 411 | 445
411 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 411 | 446
412 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 412 | 447
412 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 412 | 448
412 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 412 | 449
413 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 413 | 450
413 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 413 | 451
413 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 413 | 452
414 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 414 | 453
414 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 414 | 454
414 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 414 | 455
415 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 415 | 456
415 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 415 | 457
415 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 415 | 458
416 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 416 | 459
416 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 416 | 460
416 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 416 | 461
417 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 417 | 462
417 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 417 | 463
417 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 417 | 464
418 | Tub Room | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 418 | 465
419 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 419 | 466
419 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 419 | 467
419 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 419 | 468
420 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 420 | 469
421 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 421 | 470
421 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 421 | 471
421 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 421 | 472
422 | Conference | 14.62 | 10.12 | 7.83 | 135 | 147.9544 | 1057.05 | 422 | 473
422 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 422 | 474
422 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 422 | 475
422 | Lobby | 43.48 | 38.12 | 9.25 | 955 | 1657.4576 | 8833.75 | 422 | 476
422 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 422 | 477
422 | Trash Chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 422 | 478
423 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 423 | 479
423 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 423 | 480
423 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 423 | 481
423 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 423 | 482
424 | Linen | 22.46 | 8.19 | 7.83 | 175 | 183.9474 | 1370.25 | 424 | 483
425 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 425 | 484
425 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 425 Hall | 485
425 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 425 | 486
425 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 425 | 487
427 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 427 | 488
427 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 427 | 489
427 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 427 | 490
427 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 427 | 491
428 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 428 | 492
428 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 428 | 493
428 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 428 | 494
429 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 429 | 495
429 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 429 | 496
429 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 429 | 497
430 | Closet | 4.35 | 1.89 | 6.83 | 8 | 8.2215 | 54.64 | 430 | 498
430 | Student Room | 17.69 | 12.13 | 7.83 | 144 | 214.5797 | 1127.52 | 430 | 499
430 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 430 | 500
431 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 431 | 501
431 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 431 | 502
431 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 431 | 503
432 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 432 | 504
432 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 432 | 505
432 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 432 | 506
433 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 433 | 507
433 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 433 | 508
433 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 433 | 509
434 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 434 | 510
434 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 434 | 511
434 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 434 | 512
435 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 435 | 513
435 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 435 | 514
435 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 435 | 515
436 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 436 | 516
436 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 436 | 517
436 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 436 | 518
437 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 437 | 519
437 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 437 | 520
437 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 437 | 521
438 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 438 | 522
438 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 438 | 523
438 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 438 | 524
439 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 439 | 525
439 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 439 | 526
439 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 439 | 527
440 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 440 | 528
440 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 440 | 529
440 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 440 | 530
441 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 441 | 531
441 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 441 | 532
441 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 441 | 533
442 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 442 | 534
442 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 442 | 535
442 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 442 | 536
443 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 443 | 537
443 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 443 | 538
443 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 443 | 539
444 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 444 | 540
444 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 444 | 541
444 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 444 | 542
445 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 445 | 543
445 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 445 | 544
445 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 445 | 545
446 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 446 | 546
446 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 446 Hall | 547
446 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 446 | 548
446 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 446 | 549
446 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 446 | 550
447 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 447 | 551
447 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 447 | 552
447 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 447 | 553
448 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 448 | 554
449 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 449 | 555
451 | Storage | 16.33 | 8 | 8 | 119 | 130.64 | 952 | 451 | 556
453 | Stair | 16.33 | 11.17 | 8 | 143 | 182.4061 | 1144 | 453 | 557
501 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 501 | 558
501 | Vestibule | 11.08 | 3.48 | 7.83 | 39 | 38.5584 | 305.37 | 501 | 559
502 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 502 | 560
502 | Hall | 120.35 | 14.76 | 7.83 | 840 | 1776.366 | 6577.2 | 502 Hall | 561
502 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 502 | 562
502 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 502 | 563
503 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 503 | 564
503 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 503 | 565
503 | Student Room | 14.87 | 13.69 | 7.83 | 183 | 203.5703 | 1432.89 | 503 | 566
503 | Toilet/Shower | 7.94 | 3.92 | 7.83 | 27 | 31.1248 | 211.41 | 503 | 567
504 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 504 | 568
504 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 504 | 569
504 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 504 | 570
505 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 505 | 571
505 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 505 | 572
505 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 505 | 573
506 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 506 | 574
506 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 506 | 575
506 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 506 | 576
507 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 507 | 577
507 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 507 | 578
507 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 507 | 579
508 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 508 | 580
508 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 508 | 581
508 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 508 | 582
509 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 509 | 583
509 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 509 | 584
509 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 509 | 585
510 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 510 | 586
510 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 510 | 587
510 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 510 | 588
511 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 511 | 589
511 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 511 | 590
511 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 511 | 591
512 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 512 | 592
512 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 512 | 593
512 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 512 | 594
513 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 513 | 595
513 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 513 | 596
513 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 513 | 597
514 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 514 | 598
514 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 514 | 599
514 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 514 | 600
515 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 515 | 601
515 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 515 | 602
515 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 515 | 603
516 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 516 | 604
516 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 516 | 605
516 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 516 | 606
517 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 517 | 607
517 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 517 | 608
517 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 517 | 609
518 | Kitchenette | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 518 | 610
519 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 519 | 611
519 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 519 | 612
519 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 519 | 613
520 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 520 | 614
521 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 521 | 615
521 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 521 | 616
521 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 521 | 617
522 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 522 | 618
522 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 522 | 619
522 | Lobby | 43.48 | 38.12 | 9.25 | 808 | 1657.4576 | 7474 | 522 | 620
522 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 522 | 621
522 | Trash Chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 522 | 622
523 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 523 | 623
523 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 523 | 624
523 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 523 | 625
523 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 523 | 626
524 | Study | 8.5 | 4.5 |  | 38 | 38.25 | 0 | 524 | 627
524 | Study | 8.5 | 4.6 |  | 39 | 39.1 | 0 | 524 | 628
524 | Study | 8.5 | 4.6 |  | 39 | 39.1 | 0 | 524 | 629
524 | Study | 8.5 | 4.5 |  | 38 | 38.25 | 0 | 524 | 630
525 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 525 | 631
525 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 525 Hall | 632
525 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 525 | 633
525 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 525 | 634
527 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 527 | 635
527 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 527 | 636
527 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 527 | 637
527 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 527 | 638
528 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 528 | 639
528 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 528 | 640
528 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 528 | 641
529 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 529 | 642
529 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 529 | 643
529 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 529 | 644
530 | Closet | 4.35 | 1.89 | 6.83 | 8 | 8.2215 | 54.64 | 530 | 645
530 | Student Room | 17.69 | 12.13 | 7.83 | 144 | 214.5797 | 1127.52 | 530 | 646
530 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 530 | 647
531 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 531 | 648
531 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 531 | 649
531 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 531 | 650
532 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 532 | 651
532 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 532 | 652
532 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 532 | 653
533 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 533 | 654
533 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 533 | 655
533 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 533 | 656
534 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 534 | 657
534 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 534 | 658
534 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 534 | 659
535 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 535 | 660
535 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 535 | 661
535 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 535 | 662
536 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 536 | 663
536 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 536 | 664
536 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 536 | 665
537 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 537 | 666
537 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 537 | 667
537 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 537 | 668
538 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 538 | 669
538 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 538 | 670
538 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 538 | 671
539 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 539 | 672
539 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 539 | 673
539 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 539 | 674
540 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 540 | 675
540 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 540 | 676
540 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 540 | 677
541 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 541 | 678
541 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 541 | 679
541 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 541 | 680
542 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 542 | 681
542 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 542 | 682
542 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 542 | 683
543 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 543 | 684
543 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 543 | 685
543 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 543 | 686
544 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 544 | 687
544 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 544 | 688
544 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 544 | 689
545 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 545 | 690
545 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 545 | 691
545 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 545 | 692
546 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 546 | 693
546 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 546 Hall | 694
546 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 546 | 695
546 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 546 | 696
546 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 546 | 697
547 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 547 | 698
547 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 547 | 699
547 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 547 | 700
548 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 548 | 701
549 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 549 | 702
551 | Storage | 16.33 | 8 | 8 | 119 | 130.64 | 952 | 551 | 703
553 | Stair | 16.33 | 11.17 | 8 | 143 | 182.4061 | 1144 | 553 | 704
601 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 601 | 705
601 | Vestibule | 11.08 | 3.48 | 7.83 | 39 | 38.5584 | 305.37 | 601 | 706
602 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 602 | 707
602 | Hall | 120.35 | 14.76 | 7.83 | 840 | 1776.366 | 6577.2 | 602 Hall | 708
602 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 602 | 709
602 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 602 | 710
603 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 603 | 711
603 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 603 | 712
603 | Student Room | 14.87 | 13.69 | 7.83 | 183 | 203.5703 | 1432.89 | 603 | 713
603 | Toilet/Shower | 7.94 | 3.92 | 7.83 | 27 | 31.1248 | 211.41 | 603 | 714
604 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 604 | 715
604 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 604 | 716
604 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 604 | 717
605 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 605 | 718
605 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 605 | 719
605 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 605 | 720
606 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 606 | 721
606 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 606 | 722
606 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 606 | 723
607 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 607 | 724
607 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 607 | 725
607 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 607 | 726
608 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 608 | 727
608 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 608 | 728
608 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 608 | 729
609 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 609 | 730
609 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 609 | 731
609 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 609 | 732
610 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 610 | 733
610 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 610 | 734
610 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 610 | 735
611 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 611 | 736
611 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 611 | 737
611 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 611 | 738
612 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 612 | 739
612 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 612 | 740
612 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 612 | 741
613 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 613 | 742
613 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 613 | 743
613 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 613 | 744
614 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 614 | 745
614 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 614 | 746
614 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 614 | 747
615 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 615 | 748
615 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 615 | 749
615 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 615 | 750
616 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 616 | 751
616 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 616 | 752
616 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 616 | 753
617 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 617 | 754
617 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 617 | 755
617 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 617 | 756
618 | Tub Room | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 618 | 757
619 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 619 | 758
619 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 619 | 759
619 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 619 | 760
620 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 620 | 761
621 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 621 | 762
621 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 621 | 763
621 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 621 | 764
622 | Conference | 14.62 | 10.12 | 7.83 | 135 | 147.9544 | 1057.05 | 622 | 765
622 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 622 | 766
622 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 622 | 767
622 | Lobby | 43.48 | 38.12 | 9.25 | 955 | 1657.4576 | 8833.75 | 622 | 768
622 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 622 | 769
622 | Trash Chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 622 | 770
623 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 623 | 771
623 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 623 | 772
623 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 623 | 773
623 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 623 | 774
624 | Study | 8.5 | 4.5 |  | 38 | 38.25 | 0 | 624 | 775
624 | Study | 8.5 | 4.6 |  | 39 | 39.1 | 0 | 624 | 776
624 | Study | 8.5 | 4.6 |  | 39 | 39.1 | 0 | 624 | 777
624 | Study | 8.5 | 4.5 |  | 38 | 38.25 | 0 | 624 | 778
625 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 625 | 779
625 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 625 Hall | 780
625 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 625 | 781
625 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 625 | 782
627 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 627 | 783
627 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 627 | 784
627 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 627 | 785
627 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 627 | 786
628 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 628 | 787
628 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 628 | 788
628 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 628 | 789
629 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 629 | 790
629 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 629 | 791
629 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 629 | 792
630 | Closet | 4.35 | 1.83 | 6.83 | 8 | 7.9605 | 54.64 | 630 | 793
630 | Student Room | 17.69 | 12.13 | 7.83 | 144 | 214.5797 | 1127.52 | 630 | 794
630 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 630 | 795
631 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 631 | 796
631 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 631 | 797
631 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 631 | 798
632 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 632 | 799
632 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 632 | 800
632 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 632 | 801
633 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 633 | 802
633 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 633 | 803
633 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 633 | 804
634 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 634 | 805
634 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 634 | 806
634 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 634 | 807
635 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 635 | 808
635 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 635 | 809
635 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 635 | 810
636 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 636 | 811
636 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 636 | 812
636 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 636 | 813
637 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 637 | 814
637 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 637 | 815
637 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 637 | 816
638 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 638 | 817
638 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 638 | 818
638 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 638 | 819
639 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 639 | 820
639 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 639 | 821
639 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 639 | 822
640 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 640 | 823
640 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 640 | 824
640 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 640 | 825
641 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 641 | 826
641 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 641 | 827
641 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 641 | 828
642 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 642 | 829
642 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 642 | 830
642 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 642 | 831
643 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 643 | 832
643 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 643 | 833
643 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 643 | 834
644 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 644 | 835
644 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 644 | 836
644 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 644 | 837
645 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 645 | 838
645 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 645 | 839
645 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 645 | 840
646 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 646 | 841
646 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 646 Hall | 842
646 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 646 | 843
646 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 646 | 844
646 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 646 | 845
647 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 647 | 846
647 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 647 | 847
647 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 647 | 848
648 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 648 | 849
649 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 649 | 850
651 | Storage | 16.33 | 8 | 8 | 119 | 130.64 | 952 | 651 | 851
653 | Stair | 16.33 | 11.17 | 8 | 143 | 182.4061 | 1144 | 653 | 852
701 | Stair | 16.33 | 7.92 | 8 | 129 | 129.3336 | 1032 | 701 | 853
701 | Vestibule | 11.08 | 3.48 | 7.83 | 39 | 38.5584 | 305.37 | 701 | 854
702 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 702 | 855
702 | Hall | 120.35 | 14.76 | 7.83 | 840 | 1776.366 | 6577.2 | 702 Hall | 856
702 | Student Room | 21.27 | 8.6 | 7.83 | 141 | 182.922 | 1104.03 | 702 | 857
702 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 702 | 858
703 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 703 | 859
703 | Closet | 6.58 | 2.17 | 7.83 | 14 | 14.2786 | 109.62 | 703 | 860
703 | Student Room | 14.87 | 13.69 | 7.83 | 183 | 203.5703 | 1432.89 | 703 | 861
703 | Toilet/Shower | 7.94 | 3.92 | 7.83 | 27 | 31.1248 | 211.41 | 703 | 862
704 | Closet | 3.94 | 2 | 7.83 | 8 | 7.88 | 62.64 | 704 | 863
704 | Student Room | 21.27 | 8.6 | 7.83 | 140 | 182.922 | 1096.2 | 704 | 864
704 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 704 | 865
705 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 705 | 866
705 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 705 | 867
705 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 705 | 868
706 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 706 | 869
706 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 706 | 870
706 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 706 | 871
707 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 707 | 872
707 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 707 | 873
707 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 707 | 874
708 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 708 | 875
708 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 708 | 876
708 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 708 | 877
709 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 709 | 878
709 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 709 | 879
709 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 709 | 880
710 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 710 | 881
710 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 710 | 882
710 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 710 | 883
711 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 711 | 884
711 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 711 | 885
711 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 711 | 886
712 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 712 | 887
712 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 712 | 888
712 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 712 | 889
713 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 713 | 890
713 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 713 | 891
713 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 713 | 892
714 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 714 | 893
714 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 714 | 894
714 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 714 | 895
715 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 715 | 896
715 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 715 | 897
715 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 715 | 898
716 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 716 | 899
716 | Student Room | 26.23 | 11.94 | 7.83 | 241 | 313.1862 | 1887.03 | 716 | 900
716 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 716 | 901
717 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 717 | 902
717 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 717 | 903
717 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 717 | 904
718 | Kitchenette | 8.04 | 5.75 | 8 | 44 | 46.23 | 352 | 718 | 905
719 | Closet | 11.81 | 3.63 | 7.83 | 43 | 42.8703 | 336.69 | 719 | 906
719 | Student Room | 31.21 | 11.58 | 7.83 | 279 | 361.4118 | 2184.57 | 719 | 907
719 | Toilet/Shower | 7.1 | 3.92 | 6.83 | 24 | 27.832 | 163.92 | 719 | 908
720 | Laundry Room | 12.02 | 8.04 | 8 | 95 | 96.6408 | 760 | 720 | 909
721 | Closet | 8.04 | 3.64 | 7.83 | 29 | 29.2656 | 227.07 | 721 | 910
721 | Student Room | 26.27 | 11.6 | 7.83 | 245 | 304.732 | 1918.35 | 721 | 911
721 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 721 | 912
722 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 722 | 913
722 | Janitor | 5.23 | 2.58 | 6.83 | 13 | 13.4934 | 88.79 | 722 | 914
722 | Lobby | 43.48 | 38.12 | 9.25 | 808 | 1657.4576 | 7474 | 722 | 915
722 | Storage | 2.17 | 1.62 | 9.25 | 4 | 3.5154 | 37 | 722 | 916
722 | Trash Chute | 4.36 | 3.94 | 7.83 | 14 | 17.1784 | 109.62 | 722 | 917
723 | Closet | 8.04 | 4.03 | 7.83 | 32 | 32.4012 | 250.56 | 723 | 918
723 | Elevator | 7 | 5 | 7.83 | 35 | 35 | 274.05 | 723 | 919
723 | Student Room | 26.27 | 11.99 | 7.83 | 248 | 314.9773 | 1941.84 | 723 | 920
723 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 723 | 921
724 | Mechanical | 17.73 | 8.08 | 7.83 | 135 | 143.2584 | 1057.05 | 724 | 922
724 | Mechanical | 8.08 | 4.54 | 7.83 | 37 | 36.6832 | 289.71 | 724 | 923
725 | Closet | 3.99 | 2 | 7.83 | 8 | 7.98 | 62.64 | 725 | 924
725 | Hall | 12.53 | 10.29 | 7.83 | 97 | 128.9337 | 759.51 | 725 Hall | 925
725 | Student Room | 19.67 | 7.99 | 7.83 | 123 | 157.1633 | 963.09 | 725 | 926
725 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 725 | 927
727 | Closet | 7.71 | 7.62 | 7.83 | 58 | 58.7502 | 454.14 | 727 | 928
727 | Foyer | 10.17 | 7.56 | 7.83 | 72 | 76.8852 | 563.76 | 727 | 929
727 | Student Room | 23.92 | 17.77 | 7.83 | 347 | 425.0584 | 2717.01 | 727 | 930
727 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 727 | 931
728 | Electrical | 10.29 | 9.12 | 7.92 | 78 | 93.8448 | 617.76 | 728 | 932
728 | Storage | 10.55 | 6.12 | 7.92 | 59 | 64.566 | 467.28 | 728 | 933
728 | Storage | 10.94 | 9.04 | 7.83 | 72 | 98.8976 | 563.76 | 728 | 934
729 | Closet | 6.04 | 5.39 | 7.83 | 33 | 32.5556 | 258.39 | 729 | 935
729 | Student Room | 21.64 | 15.37 | 7.83 | 244 | 332.6068 | 1910.52 | 729 | 936
729 | Toilet/Shower | 5.75 | 4.67 | 6.83 | 22 | 26.8525 | 150.26 | 729 | 937
730 | Closet | 4.35 | 1.89 | 6.83 | 8 | 8.2215 | 54.64 | 730 | 938
730 | Student Room | 17.69 | 12.13 | 7.83 | 144 | 214.5797 | 1127.52 | 730 | 939
730 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 730 | 940
731 | Closet | 8.04 | 4.53 | 7.83 | 35 | 36.4212 | 274.05 | 731 | 941
731 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 731 | 942
731 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 731 | 943
732 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 732 | 944
732 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 732 | 945
732 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 732 | 946
733 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 733 | 947
733 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 733 | 948
733 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 733 | 949
734 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 734 | 950
734 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 734 | 951
734 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 734 | 952
735 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 735 | 953
735 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 735 | 954
735 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 735 | 955
736 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 736 | 956
736 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 736 | 957
736 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 736 | 958
737 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 737 | 959
737 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 737 | 960
737 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 737 | 961
738 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 738 | 962
738 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 738 | 963
738 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 738 | 964
739 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 739 | 965
739 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 739 | 966
739 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 739 | 967
740 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 740 | 968
740 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 740 | 969
740 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 740 | 970
741 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 741 | 971
741 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 741 | 972
741 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 741 | 973
742 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 742 | 974
742 | Student Room | 21.27 | 11.94 | 7.83 | 191 | 253.9638 | 1495.53 | 742 | 975
742 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 742 | 976
743 | Closet | 8.04 | 2.2 | 7.83 | 18 | 17.688 | 140.94 | 743 | 977
743 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 743 | 978
743 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 743 | 979
744 | Closet | 8.04 | 3.99 | 7.83 | 31 | 32.0796 | 242.73 | 744 | 980
744 | Student Room | 26.27 | 11.94 | 7.83 | 249 | 313.6638 | 1949.67 | 744 | 981
744 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 744 | 982
745 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 745 | 983
745 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 745 | 984
745 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 745 | 985
746 | Closet | 8.34 | 7.54 | 7.83 | 61 | 62.8836 | 477.63 | 746 | 986
746 | Hall | 91.29 | 27.95 | 7.83 | 692 | 2551.5555 | 5418.36 | 746 Hall | 987
746 | Sink Room | 6.99 | 4.83 | 6.83 | 27 | 33.7617 | 184.41 | 746 | 988
746 | Student Room | 17.64 | 16.12 | 7.83 | 222 | 284.3568 | 1738.26 | 746 | 989
746 | Toilet/Shower | 7.33 | 2.5 | 6.83 | 18 | 18.325 | 122.94 | 746 | 990
747 | Closet | 8.04 | 2.2 | 7.83 | 17 | 17.688 | 133.11 | 747 | 991
747 | Student Room | 17.27 | 10.14 | 7.83 | 126 | 175.1178 | 986.58 | 747 | 992
747 | Toilet/Shower | 8.02 | 3.92 | 6.83 | 27 | 31.4384 | 184.41 | 747 | 993
748 | Study | 6.75 | 5.2 | 7.83 | 35 | 35.1 | 274.05 | 748 | 994
749 | Study | 7 | 5.94 | 7.83 | 42 | 41.58 | 328.86 | 749 | 995
751 | Storage | 16.33 | 8 | 8 | 119 | 130.64 | 952 | 751 | 996
753 | Stair | 16.33 | 11.17 | 8 | 143 | 182.4061 | 1144 | 753 | 997
801 | Stair | 20.48 | 12.69 | 8 | 179 | 259.8912 | 1432 | 801 | 998
803 | Storage | 20.48 | 7.94 | 8.53 | 146 | 162.6112 | 1245.38 | 803 | 999
824 | Mechanical | 23.6 | 12 | 8.17 | 265 | 283.2 | 2165.05 | 824 | 1000
827 | Mechanical | 21.01 | 5.42 | 8.08 | 110 | 113.8742 | 888.8 | 827 | 1001
851 | Storage | 16.33 | 8 | 8.08 | 119 | 130.64 | 961.52 | 851 | 1002
853 | Stair | 16.33 | 11.17 | 8 | 143 | 182.4061 | 1144 | 853 | 1003
|  |  |  | net sf | 103678
|  |  |  | assigned sf | 75327
|  |  |  | total gross sf | 125020
|  |  |  | B gross sf | 17666
|  |  |  | 1 gross sf | 10991
|  |  |  | 2 gross sf | 16000
|  |  |  | 3 gross sf | 15711
|  |  |  | 4 gross sf | 16000
|  |  |  | 5 gross sf | 15711
|  |  |  | 6 gross sf | 16000
|  |  |  | 7 gross sf | 15711
|  |  |  | 8 gross sf | 1230